## Cover Sheet (hidden)
Elyzer P-300 Safety Matrix (INTERNAL)
Projekt, Kande / Project, Customer:
ELYP-300_PFA020_Safety-Matrix
Projekt-Nr. / Project-No.: |  | DCC |  | Handhabung/Handling |  | Version
|  | PFA020 |  | Restricted |  | 3.3
Produkt / Product:
Elyzer P-300 Reference Plant
US/EU Export Controls *) |  | ECCN: | N | AL: | N
Ersteller (Name, Abteilung) / Author (Name, Department):
SE TI SES HS EN PSE SE TI SES HS EN AC |  |  | Merkl, Bernd Reinhart, Florian
Abteilung / Department |  |  | Name |  | Unterschrift / Signature
Konformitätsprüfung / Conformity check:
Abteilung / Department |  |  | Name |  | Unterschrift / Signature
Fachliche Prüfung (optional) / Technical review (optional):
SE TI SES HS EN PSE SE TI SES HS EN ELP SE TI SES HS EN ELP |  |  | Schwager, Julius Benninghoff, Moritz Niedernhuber, Josef
Abteilung / Department |  |  | Name |  | Unterschrift / Signature
Verantwortliche Freigabe / Responsible for release
SE TI SES PRM PLM |  |  | Bäzner, Thorsten
Abteilung / Department |  |  | Name |  | Unterschrift / Signature
*)
Die mit "AL ≠ N" gekennzeichneten Güter unterliegen bei der Ausfuhr aus der EU der europäischen bzw. deutschen Ausfuhrgenehmigungspflicht. Die mit "ECCN ≠ N" gekennzeichneten Güter unterliegen der US-Reexportgenehmigungspflicht. Auch ohne Kennzeichen, bzw. bei Kennzeichen "AL:N" oder "ECCN:N" kann sich eine Genehmigungspflicht, unter anderem durch den Endverbleib and Verwendungszweck der Güter, ergeben.
Goods labeled with "AL ≠ N" are subject to European or German export authorization when being exported out of the EU. Goods labeled with "ECCN ≠ N" are subject to US reexport authorization. Even without a label, or with label "AL:N" or "ECCN:N", authorization may be required due to the final whereabouts and purpose for which the goods are to be used.
Version | Ersteller | Department | Date | Description
2.0 | B. Merkl | SE TI SES HS EN PSE | 2023-10-10 | Major Revision, Split of Plant & Array part
3.0 | B. Merkl | SE TI SES HS EN PSE | 2023-11-16 | Major revision, new rectifier system
3.2 | B. Merkl | SE TI SES HS EN PRE | 2024-07-04 | Major revision, deletion of pol. rect.
3.3 | B. Merkl | SE TI SES HS EN PRE | 2025-05-13 | Renamed BoP to Ely Block and Array to Ely System; see marks "V3.3"

## BOP - SIS
| Safety Functions IEC61511 Balance of Plant - H2Sakura - has to be adjusted project specifically - S --> storing, reset required / speichernd, rücksetzen erforderlich N --> non storing, no reset required / nicht speichernd, rücksetzen nicht erforderlich NP--> non storing purge, reset when purge is finished or canceled / nicht speichernde Spülung, Rücksetzen wenn Spülung beendet oder abgebrochen S* --> storing, reset required / speichernd, rücksetzen erforderlich, not implemented as SIL-rated safety function (IEC61511) N* --> non storing, no reset required / nicht speichernd, rücksetzen erforderlich, not implemented as SIL-rated safety function (IEC61511) NP*--> non storing purge, reset when purge is finished or canceled / nicht speichernde Spülung, Rücksetzen wenn Spülung beendet oder abgebrochen, not implemented as SIL-rate safety function (IEC61511) Remark: Cause & effects listed in "BoP - SIS" must be implemented in SIS plant control (by others). Effect signals (actions) listed herein shall be communicated to array control (mandatory). As alternative single signals must be provided to array controls in order to implement the cause&effects in array control logic (optional). | [12 empty] | Effect Identifier | ARY1_TRIP | ARY1_TRIP_N2_PRG | ARY1_TRIP_N2_BLK | ARY1_PRD_VLV_CLS | CMPR_STO
[14 empty] | Effect Description | Array X - Safety Trip | Array x - Safety Trip with N2 Purge | Array X - Safety Trip and Block N2 Purge | Array X - Product Valve | Compressor stop and closing of upstream H2 valve
[14 empty] | Value | 0 | 0 | 0 | 0 | 0
[14 empty] | Output Tag | =K01CCA01KF001-KZ51;YV01 (To =G0xNHY01KF001-KZ01;XV01) | =K01CCA01KF001-KZ53;YV01 (To =G0xNHY01KF001-KZ03;XV01) | =K01CCA01KF001-KZ54;YV01 (To =G0xNHY01KF001-KZ04;XV01) | =K01CCA01KF001-KZ55;YV01 (To =G0xNHY01KF001-KZ05;XV01) | =K01CCA01KF001-KZ56;YV01 (To =V01NHC30KF001-KZ01;XV01)
[14 empty] | Action | off | start | off | close | stop
Customer Revision | Cause Identifier | Chgd | Input Tag | Signal | Warn | Safety Limit | Hyst. | Unit | Delay | Func 1 | Func 2 | Cause Description | Comment | [6 empty] | Response Time | Response Time | Comments/Remarks | Comments, Causes / Kommentare, Ursachen | Test date/result | Test executed by | Revision history /internal comments
Interconnecting Piping
A | H2_BLW_OFF_BLKD | 3.3 | V01NHC10WP001-QMxx (isolation shut off valve of H2 PSV relief line - ElySys ny) | - | - | 0 | - | BOOL | _ |  | 1oox | H2 Blow off line blocked | Isolation Valve blow line H2 not open |  |  |  | N* |  |  |  |  | Not applicable as no isolation valve in common vent header connecting outlet of safety relief valve and blowoff valve | Array must not start when H2 blow off line is blocked (e.g. after maintenance), N2 purge must also be blocked, except a SIS purge is required. XXXXX isolation valve is in common vent header considered under customer's scope, not applicable if no isolation valve is in common vent header
A |  |  | V01NHC10WP001-QMxx (isolation shut off valve of H2 blow off line - ElySys ny) | - | - | 0 | - | BOOL | _
A | H2_PRD_LIN_BLKD | 3.3 | V01NHC10WP001-QMxx (isolation shut off valve of H2 product gas line - ElySys ny) | XB02 | - | 0 | - | BOOL | _ |  | 1oo1 | H2 Product gas line blocked | Isolation valve downstream of H2 PGV not openden |  |  |  |  | N* | N* |  |  | 1. Cutomer to check and integrate automatic isolation valve between H2 product valve and compressor with the desired effect. 2. BOP ready (Product Gas Clearance) must not be given when downstream isolation valve is blocked/closed | Product Gas Clearance must not be given when downstream isolation valve is blocked
Buffer Tank
A | LVLPRS_BFR_TNK_HH | 3.3 | V01NHC20CM001-BPxx | XQ01 | AH 100 | AZHH 110 | 5.0 | mbar(g) | - |  | 1oo1 | Pressure transmitter high value downstream of product control valve | Pressure exceeding beyond recommeneded value of 80 mbar(g) at downstream of product control valve |  | S* |  |  | S* | S* | 1 s | 1 s | Trip limits are defined as per the interface document "DP21T-7000287800_ElyP-300_Interface definition_H2-PGV" Recommeded operating range to be maintained as "70 to 80 mbar(g); short term (5s) 85 mbar(g) " | Trip limits are project specific and depend on tank size and shall be considered with 10-15% margin above temrinal end values. Shut down of array is one possible solution and depends on project specific design of compressor (redundancy etc.) and recommendation of customer. It may also be possible to keep arrays running and close the product gas valves, but then the buffer tank needs to be sized accordingly. |  |  | V3.2, 24.04.2024, BM: Neu eingefügt aus betrieblichen Teil. Funktion muss unabhängig sein von einem Reglerfehler im System Schrank, deshalb im fehlersicheren Teil. Immediate shutdown to avoid bigger sizing of buffer tank due to closing time of product gas valve (which would be the alternative solution). V3.2, BM, 14.05.2024: AZHH changed to ASHH since not SIL rated V3.3, BM: deleted "and compressor is running"
A | LVLPRS_BFR_TNK_LL | 1.4 | V01NHC20CM001-BPxx | XQ01 | AH 65 | AZHH 60 | 5.0 | mbar(g) | - |  | 1oo1 | Pressure transmitter low value downstream of product control valve | Pressure decreased beyond recommeneded value of 70 mbar(g) at downstream of product control valve |  | S* |  |  | S* | S* | 5 s PCV (if applicable) | 1 s |  | Pressure level control, operational trip of subsequent gas systems, - quality of compressor stop is dependent on selected compressor and corresponding process response time. This must be evaluated during project specific HAZOP. Finally an underpressure must be prevented inside buffer tank to avoid damage and ingress of air. - closing of product gas valve is optionally (performed in array control, if pressure on H2 is low) - must also be evaluated on a project specific basis |  |  | V1.4 (FR): - Stop of compressor changed from "S*" to "S". - Close Product Valve changed from "N" to "S" - Changed hysteresis from 30.0 to 15.0 for consistency with operational trip V2.0, 29.08.2023: (JS, BM, RW, GL, FH, FR): compressor stop in S, based on reference HAZOP
A |  |  | V01NHC30KF001-KZ01 | XG01 | - | 0 | - | BOOL | - |  |  | 0 = Compressor feedback running
Emergency Stop
A | EM_STOP_PLANT | 3.1 | further ESD commamnds |  | - | 0 | - | BOOL | - |  | 1ooX | Emergency Stop Plant |  |  |  | S* |  |  | S* | 1s | 1 s | -Manual Pushbuttons or automatic signal from customer side (Eg. Earthquake activity etc.) - TBC If only H2 shall be purged or if O2 & H2 side shall be prurged in ESD at all (depends on sizing of N2 supply) | -Manual Pushbuttons or software -project specific - TBC IF ONLY H2 SHALL BE PURGED OR IF O2 & H2 SIDE SHALL BE PURGED IN ESD AT ALL (depends on sizing of N2 supply). - TBD if emergency push button shuts down only respective electrolyzer or all electrolyzers at same same time for multi array plants (in case two different ES_STOPs shall be considered: individual for array vs. overall plant) - preliminary: N2 supply must be designed to purge O2 and H2 side for all simultaneously triggered arrays |  |  | 28.08.2023: in case project specific HAZOP defines S, it must be check if SIL quality is possible 29.08.2023: (JS, BM, RW, GL, FH): typical failures to push EM-STOP: electrical failures, leakages - at least one push button per building, in addition one push button per array 31.08.2023: - N2 supply must be designed to purge O2 and H2 side for all simultaneously triggered arrays V3.1 2024-01-17 (RW, BM, FR): K01CKY01KF001-SF01 deleted since not existent, manual pushbutton has 2-channel-evalution (XW01/XW02) V3.1, 2024-01-17 (RW, FR, BM): comment deleted
A |  |  | K01CSY01UH001-SF01 | XW01/02
Fire & Gas Alarm
A | GAS_SYS_ELY | 3.1 | K01CKB01BQ001-BQ01 | XW01 | AH 5.0 | AZHH 25.0 | proof of purge | % LEL | - |  | 1oo1 | H2 Gasalarm Electrolyzer Hall |  |  |  | S* |  |  | S* | 10s | 10s |  | - Project specific: TBD if depressurization (opening of blow off valves and closing of product gas valve) of Array must be implemented as SIL function. - project specific: TBD if only respective electrolyzer or all electrolyzers are purged at same time for multi array plants (dependending on position and number of gas sensors/design of building) - N2 supply must be designed to purge O2 and H2 side for all simultaneously triggered arrays |  |  | 28.08.2023: in case project specific HAZOP defines "S", it must be check if SIL quality is possible. 29.08.2023: (JS, BM, RW, GL, FH): gas sensors are not considered as primary protection against hazardous zones and therfore not considered as SIL rated function. 31.08.2023: - N2 supply must be designed to purge O2 and H2 side for all simultaneously triggered arrays V3.1, 2024-01-17 (RW, FR, BM): comment deleted
A | FIRE_SYS_ELY | 3.1 | K01CKA01BR001-BR01 | XW01 | 0 | 0 | proof of purge or no fire alarm | BOOL | - |  | 1oo1 | Fire & Smoke Alarm Electrolyzer Hall |  |  |  | S* |  |  | S* | 10s | 10s |  | - Project specific: TBD if depressurization (opening of blow off valves and closing of product gas valve) of Array must be implemented as SIL function - project specific: TBD if only respective electrolyzer or all electrolyzers are purged at same time for multi array plants (dependending on position and number of gas sensors/design of building) - N2 supply must be designed to purge O2 and H2 side for all simultaneously triggered arrays |  |  | 28.08.2023: in case project specific HAZOP defines "S", it must be check if SIL quality is possible. 29.08.2023: (JS, BM, RW, GL, FH): causes for fire must be defined project specifically, dependent on local site conditions. Fire and Gas sensors are not considered as primary protection to prevent dangerous conditions and therfore not considered as SIL rated function. 31.08.2023: - N2 supply must be designed to purge O2 and H2 side for all simultaneously triggered arrays V3.1, 2024-01-17 (RW, FR, BM): comment deleted
Note:
1 | ARY1_TRIP_N2_PRG Effect : Array trip with N2 purge command inherently provides command for product valve closure
2 | Tags indicated in Input tags as "V01, K01,QMxx" are shown as per Siemens Energy's RDSPP Tagging philosophy, customer's tagging may br different and can be adpated
3 | The cause-and-effect relationships outlined herein are provided solely on the basis of Siemens Energy’s limited experience with complete plant configurations. They are intended for preliminary guidance only and shall not be construed as comprehensive, exhaustive, or finalized from Siemens Energy’s side.
The Customer shall bear full responsibility for conducting detailed investigations, including but not limited to project-specific HAZOP and HAZID studies, to identify any critical causes at the complete plant level that may trigger array safety-related effects.
Any additional causes or effects identified by the Customer may be proposed for inclusion. Incorporation into the safety matrix and associated logic shall be subject to mutual agreement between Siemens Energy and the Customer.
Note on T12: Mahor, Abhishek (ext): Product valve close and compressor stop adapted

## BOP - Operational
| Operational Protection Balance of Plant - H2 Sakura - has to be adjusted project specifically - S --> storing, reset required / speichernd, rücksetzen erforderlich N --> non storing, no reset required / nicht speichernd, rücksetzen nicht erforderlich NP--> non storing purge, reset when purge is finished or canceled / nicht speichernde Spülung, Rücksetzen wenn Spülung beendet oder abgebrochen Remark: Cause & effects listed in "BoP - Operation" must be implemented in plant control (by others). Effect signals (actions) listed herein shall be communicated to array control (mandatory). As alternative single signals must be provided to array controls in order to implement the cause&effects in array control logic (optional). | [13 empty] | Effect Description | Array X - Trip | Array X - Trip with N2 Purge | Array X - Product Gas Release | Array Y - Product Gas Release | Array X - Demin Supply Valve | Demin Water Pump | 2nd Ventilator on / Ventilator full speed | Cooling Water Pump 1 | Cooling Water Pump 2 | Vent Buffer | Stop Compressor | Stop DeOxo | Buffer Tank - Inert required | Buffer Tank - H2 ready | Plant Shut down SLC |  | 1. There is no specific constant pressure piston buffer tank in H2 Yes project downstream of product control valve. Hence customer's scope constant buffer tank volume (downstream of product control valve) to be reffered as buffer tank/volume . 2) ARY1_TRIP_N2_PRG Effect : Array trip with N2 purge command inherently provides command for product valve closure
[15 empty] | Value | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1
[15 empty] | Output Tag | =K01CCA01KF11x;YV01 (To =G0xNHY01KF101-KZ75;XV01) | =K01CCA01KF11x;YV03 (To =G0xNHY01KF101-KZ77;XV01) | =K01CCA01KF11x;YV04 (To =G0xNHY01KF101-KZ78;XV01) | =K01CCA01KF11y;YV04 (To =G0yNHY01KF101-KZ78;XV01) | =K01CCA01KF11x;YV05 (To =G0xNHY01KF101-KZ79;XV01) | =A01GCF01GP001-GP01/GP02;YB21 | =XAU01UN001-CG01 =XAU01UN001-CG02 | =A01PAD01GP001-GP01;YB21 | =A01PAD01GP001-GP02;YB21 | =V01NHC30WP001-QM02;YB21 | =V01NHC30KF201 | =V01NHC40KF201 | =V01NHC20KF201 | =V01NHC20KF203 | =K01CSY01KF102
[15 empty] | Action | off | off | off | off | close | off | on | off | off | open | off | off | on | off | start
Customer Revision | PLS# | Chgd | Input Tag | Signal | Warn | Switch/Limit | Hyst. | Unit | A_DC | A_DG | Func 1 | Func 2 | Cause Description | Comment | [16 empty] | Comments/Remarks | Comments, Causes / Kommentare, Ursachen | Test date/result | Test executed by | Revision history /internal comments
A |  |  | K10CCA01UH001-KZ50 | XM01 | - | 1 | - | BOOL | 5s |  |  |  | Block - Com Fault to Plant CPU | via AS-AS Communication |  | N
A |  |  | K10CCA01UH001-KZ51 | XM01 | - | 1 | - | BOOL |  |  |  |  | Block - Trip Arrays(from Plant) | via AS-AS Communication |  | N
A |  |  | K10CCA01UH001-KZ52 | XV01 | - | 0 | - | BOOL |  |  |  |  | Block - Trip with N2 Purge Arrays (from Plant) | via AS-AS Communication |  |  | N
A |  |  | K10CCA01UH001-KZ53 | XV01 | - | 0 | - | BOOL |  |  |  |  | Close Array Product Valves (from Plant) | via AS-AS Communication |  |  |  |  | N
A |  |  | K10CCA01UH001-KZ54 | XV01 | - | 0 | - | BOOL |  |  |  |  | Block - Trip Compressor (from Plant) | via AS-AS Communication | [11 empty] | N
A |  |  | K10CCA01UH001-KZ55 | XV01 | - | 0 | - | BOOL |  |  |  |  | Block - Close General Product Handover Valve (from Plant) | via AS-AS Communication
Electrolyzer
A |  | 1.1 | K01CCA01KF11x (From G0xNHY01KF102;YV01) | XV01 | - | 0 | - | BOOL | - | - |  | 1ooX | Buffer Tank - Set Inert Required (from Array 1) | from Array 1 via AS-AS communication, no message |  | S |  | S | [7 empty] | S |  | S
A |  | 1.1 | K01CCA01KF11x (From G0xNHY01KF102;YV02) | XV01 | - | 0 | - | BOOL | - | - |  | 1ooX | Buffer Tank - Reset H2 Ready (from Array 1) | from Array 1 via AS-AS communication, no message | [14 empty] | S
| Ambient Gas Warning | [30 empty] | Warning: Country specific requirements DE: separation is required.
A |  | 1.1 | K01CKB01BQ001-BQ01 | XQ01 | AH 0.8 | - | proof of purge for electrolyzer hall from BOP | % LEL | - | - |  | 1ooX | H2 Sensor Electrolyzer Hall - Warning | [18 empty] | project specific tbd
A |  | 1.1 | K01CKB01BQ001-BQ01 | XQ01 | - | ASHH 1.0 |  | % LEL | - | - |  | 1ooX | H2 Sensor Electrolyzer Hall - Alarm |  |  | S |  | S | S |  |  | S |  |  |  | S | [5 empty] | project specific tbd
A |  | 1.1 | K01CKB01BQ001-BQ02 | XQ01 | AH 0.8 | - | proof of purge for electrolyzer hall from BOP | % LEL | - | - |  | 1ooX | H2 Sensor Ventilation - Warning | [18 empty] | project specific tbd
A |  | 1.1 | K01CKB01BQ001-BQ02 | XQ01 | - | ASHH 1.0 |  | % LEL | - | - |  | 1ooX | H2 Sensor Ventilation - Alarm |  |  | S |  | S | S |  |  | S |  |  |  | S | [5 empty] | project specific tbd
A |  | 1.1 | K01CKB01BQ001-BQ03 | XQ01 | AH 0.8 | - | proof of purge for electrolyzer hall from BOP | % LEL | - | - |  | 1ooX | H2 Sensor Buffer tank - Warning
A |  | 1.1 | K01CKB01BQ001-BQ03 | XQ01 | - | ASHH 1.0 |  | % LEL | - | - |  | 1ooX | H2 Sensor Buffer tank - Alarm | stop venting at H2 Buffer Level low low |  | S |  | S | S | [5 empty] | N | S | S |  |  |  | Effect shown are recommendation from SE, customer to decide if need to be implemented considering the ambient conditions | actions tbd project specific
A |  | 1.1 | K01CKA01BQ001-BQ04 | XG01 | 0 | - | - | BOOL | - | - |  | 1ooX | Gas Alarm Overall Plant (H2) | [18 empty] | project specific tbd
Instrument Air
A |  | 3.3 | A01QFB01QM001-BP01 | XQ01 | AL 5.5 | ASLL 5.0 | 1.0 | bar(g) | 5 s | 5 s |  | 1oo1 | Low Pressure Instrument Air Supply |  |  |  | S | [14 empty] | project specific limit based on tank size If there is no potential ingress of air into the system (e.g. by ensured N2-blanketed blow off line) it might be discussed, if a N2 purge is necessary (needs be evaluated during HAZOP based on downstream system design). Buffer volume of tank when reaching trip limit needs to be big enough to allow shutdown and inertization of plant. Minimum supply pressure for valves is 4,5 barg to shut down the plant. |  |  | V3.2: 8.03.2024 (BM): added: "If there is no potetial of ingress of air into the system (e.g. by ensured N2-blanketed blow off line) it might be discussed, if a N2 purge is necessary (needs be evaluated during HAZOP based on downstream system design)." V3.3, BM, RK, 2024-11-14: warning reduced from 6 to 5,5 and alarm reduced from 5,5 to 5 barg.
A |  | 3.3 | A01QFB01QM001-BP02 | XQ01 | AL 5.5 | ASLL 5.0 | 1.0 | bar(g) | 5 s | 5 s |  | 1oo1 | Low Pressure Instrument Air Storage Pressure Low |  |  |  | S | [8 empty] | S |  |  |  |  | 1. Limit is based on tank size and the end requirement at SE's electrolyzer 2. Buffer volume of tank when reaching trip limit needs to be big enough to allow shutdown and inertization of plant, Minimum supply pressure for valves is 6 barg to shut down the plant.
N2 Supply
A |  | 3.2 | A01QJB01GZ001-BL01 | XQ01 | AL 2000 | ASLL 420 | 50 | l | 5 s | - |  | 1ooX | Liquid N2 Tank Level Low |  |  |  | S | [10 empty] | (S) |  |  |  | project specific limit based on tank size, purge before N2 empty. Multi Array: limit must be high enough to purge all arrays (prel. purge volume 106 Nm³ per array) Important note: This limit starts purge of all arrays. Thus, the normal filling level must be higher to avoid running into this limit if normal operational purging is active If other systems than array need N2 purge must be decided project specifically and may require to change limit settings. If there is no potential ingress of air into the system (e.g. by ensured N2-blanketed blow off line) it might be discussed, if a N2 purge is necessary (needs be evaluated during HAZOP based on downstream system design). |  |  | V2.0: 2023-08-31: (BM, FR): comment for other systems added. V3.2: 8.03.2024 (BM): added: "If there is no potetial of ingress of air into the system (e.g. by ensured N2-blanketed blow off line) it might be discussed, if a N2 purge is necessary (needs be evaluated during HAZOP based on downstream system design)."
A |  | 1.3 | A01QJB01WP001-BP01 | XQ01 | AL XX | ASLL XX | - | bar(g) | 5 s | 60 s |  | 1oo1 | Low Pressure Main N2 Supply |  |  | S |  | S | [7 empty] | S | [5 empty] | project specific, if no liquid N2 tank is used, The inertisation step sequence must be started based on a pressure low limit. Pressure limit must be equal to a reserve of two times purge volume. Purge time : To be specified for customer Purge Volume : To be specified for customer Flow rate : To be specified for customer |  |  | V1.3: comment added
A |  | 3.3 | Blanketing of H2 blow off lance (project specific) |  |  | 0 |  | Vol % | 5 min | 60 s |  | 1ooX | N2 blanketing of H2 blow off line not active |  |  | S | [15 empty] | Interlock of Rectifier. If plant is shut down during operation and if a N2 purge can be performed depends on kind of nitrogen supply and must be evaluated during project specific HAZOP. IF APPLIICABLE), SE's considrering seoarate purging source for downstream purging other than electrolyzer |  |  | V3.3, BM, 2024-11-06: Implemented to not forget to define a cause if a N2 blanketing of blow off lance is applicable in a project
|  | 1.4 | A01QJB01WP003-QM11 | XB02 | - | 0 | - | BOOL | 2 s | 1 s |  | 1oo1 | N2 purging of product gas line | no messages for this cause |  | S | [12 empty] | S |  |  | For purging downstream of product control valve
Ventilation & Temp. Electrolyzer Hall
A |  | 1.1 | X01XAL01GQ001-BFxx |  | 0 | 0 | - | BOOL | 50 s | - |  | YooX | Flow Monitoring Ventilation |  |  | S |  | S | [7 empty] | S |  |  |  |  | Based on ventilation requirements | project specific based on ventilation requirements
A |  | 1.1 | X01XAL01KF001-BT01 | XQ01 | AL 5.0 | ASLL 2.0 | 2.00 | °C | 15 min | - |  | 1oo1 | Temp. Low Electrolyzer Hall | [17 empty] | Interlock for rectifier startup | Interlock for rectifier startup
A |  | 1.1 | X01XAL01KF001-BT01 | XQ01 | AH 40.0 | ASHH 45.0 | 2.00 | °C | 15 min | - |  | 1oo1 | Temp. High Electrolyzer Hall |  |  | S | [14 empty] | normally limited by gas monitoring system | project specific, normally limited by gas monitoring system
Demin Water Supply
A |  | 1.1 | A01GCF01CM001-BL01 | XQ01 | AL 40.0 | ASLL 30.0 | 2.00 | cm | 1 s | - |  | 1oo1 | Low Level Demin Water Tank | level above suction nozzle of pump | [5 empty] | S | S | [9 empty] | 1. Values to be defined by customer to ensure SE's terminal requirementc, should be implemented in black box 2. Pump off command is recommended from SE however customer to decide and consider its implications | Values project specific, should be implemented in black box
A |  | 3.2 | A01GCF01GP001-BP01 | XQ01 | AL 0.8 | ASLL 0.5 | 0.3 | bar(g) | 5 s | - |  | 1oo1 | Low Pressure Demin Water Supply | [6 empty] | S | S | [9 empty] | 1. Backflow Prevention, should be implemented in black box. 2. Pump off command is recommended from SE however customer to decide and consider its implications | Backflow Prevention, should be implemented in black box. It can be decided project specifically to also shut down the respective arrays, in order to avoid running into a low level scenario. |  |  | V3.2, 2024-04-04, BM: "It can be decided project specifically to also shut down the respective arrays, in order to avoid running into a low level scenario." eingefügt
A |  | 1.4 | A01GCF01GP001-BP01 | XQ01 | AH 3.2 | ASHH 3.5 | 0.2 | bar(g) | 10 s | - |  | 1oo1 | High Pressure Demin Water Pump |  |  | S |  | S |  | S | S |  |  |  |  | S |  |  |  |  | 1. Limit values increased (supply pressure is specified with 25 to max 30 m). Rectifier shut down not mandatory. 2. Pump off command is recommended from SE however customer to decide and consider its implications | Values project specific. Limit values increased (supply pressure is specified with 25 to max 30 m). Rectifier shut down not mandatory. |  |  | V1.4 (FR): added interlock of Demin Supply Valve
A |  | 3.2 | A01GCF01GP001-BQ01 | XQ01 | AH 0.25 | ASHH 0.2 | 0.2 | µS/cm | 10 min | - | and | 2oo2 | Bad Quality Demin Water Supply |  |  | S |  | S | [7 empty] | S |  |  |  |  | Values as per SE's process water quality requirement | Values project specific |  |  | V3.2, 2024-03-04 (BM): G01NHY01KF101/KZ12;XB01 added to avoid interlock if demin water is standing in pipe. Trip changed from 12 to 5 µS/cm since only valid in operation. DC inreased from 5 to 10 min
A |  |  | G0xNHY01KF101/KZ12 | XB01 | - | 1 | - | BOOL |  |  |  |  | 1= Array in operation
A |  | 1.1 | A01GCF01KF001-KF0x | XU01 | 0 | 0 | - | BOOL | - | - |  | 1oo1 | Demin Water Unit Common Fault |  |  | S |  |  |  | S | S
Cooling Water Supply
A |  | 1.1 | A01PAD01GP001-BP03 | XQ01 | AL 0.8 | ASLL 0.5 | 0.2 | bar(g) | 1 min | - |  | 1oo1 | Low Pressure Cooling Water Supply |  |  | S | [6 empty] | S | S | [7 empty] | Delay shutoff of cooling pumps by additional 5s (project specific)
A |  | 3.2 | A01PAD01GP001-BP03 | XQ01 | AH 2.5 |  | 0.1 | bar(g) | 20 s | - |  | 1oo1 | High Pressure Cooling Water Supply | [18 empty] | Warning. Values and Limit project specific |  |  | V3.2, 2024-04-05, BM: added "Warning"
A |  | 1.1 | A01PAD01GP001-BP01 | XQ01 | AH 4.8 | ASHH 5.0 | 0.2 | bar(g) | 20 s | - |  | 1oo1 | Min Flow Protection Cooling Pump 1 (dp high) |  |  | S |  | S |  |  |  |  | S |  |  | S | [5 empty] | Values and Limit project specific
A |  | 1.1 | A01PAD01GP001-BP02 | XQ01 |  | H 5.0 | 0.2 |  | 20s | - |  | 1oo1 | Min Flow Protection Cooling Pump 2 (dp high) | [10 empty] | S
A |  | 1.1 | A01PAD01GP001-BP01 | XQ01 | AL (SP -0.1) | ASLL (SP -0.2) | 0.1 | bar(g) | 5 s | - |  | 1oo1 | Pump Switch Over (set point deviation) | when Pump 1 is running | [8 empty] | S | [7 empty] | 1. Warning. Values and Limit to be defined by customer to ensure SE's terminal requirement 2. Pump off command is recommended from SE however customer to decide and consider its implications | Values and Limit project specific
A |  | 1.1 | A01PAD01GP001-BP02 | XQ01 |  | H 5.0 | 0.2 |  | 20s |  |  | 1oo1 |  | when Pump 2 is running | [9 empty] | S
A |  | 1.1 | A01PAD01WP001-BP01 | XQ01 | AH 5.8 | ASHH 6.0 | 0.1 | bar(g) | - | - |  | 1oo1 | High Pressure Pump Discharge |  |  | S |  | S |  |  |  |  | S | S |  | S | [5 empty] | Values and Limit project specific
Buffer Tank
A |  | 3.2 | V01NHC20CM001-BPxx | XQ01 | AH 100 | ASHH 110.0 | 15 | mbar(g) | 1 s | - |  | 1oo2 | Pressure transmitter high value downstream of product control valve | [17 empty] | Trip limits are defined as per the interface document "DP21T-7000287800_ElyP-300_Interface definition_H2-PGV" Recommeded operating range to be maintained as "70 to 80 mbar(g); short term (5s) 85 mbar(g) " | Trip limits are project specific and depend on tank size. Shut down of array is one possible solution and depends on project specific design of compressor (redundancy etc.) and recommendation of customer. It may also be possible to keep arrays running, but then the buffer tank needs to be sized accordingly. |  |  | V1.3: second level sensor added V3.2, 24.04.2024, BM: shifted to BoP-SIS, Trip needs to be independent from operational CPU/logic
A |  |  | V01NHC20CM001-BPxx | XQ01 | AL 65.0 | ASLL 60.0 | 15.0 | mbar |  |  |  |  | Pressure transmitter low value downstream of product control valve |  |  | S |  | S | [7 empty] | S | S
A |  | 1.4 | V01NHC20CM001-BL02 | XQ01 | AL 15.0 | ASLL 10.0 | 15.0 | % | - | - |  | 1oo1 | H2 Buffer Level Pressure Low Low | [12 empty] | S | S |  |  |  |  | It may be possible to bring the compressor in recycle mode instead of shutting it down (project specific). |  |  | V1.4 (FR): changed hysteresis from 30% to 15%, because we can have only one hysteresis for the measurement value
A |  | 3.1 | H2 Buffer Level Low Low |  | - | 1 | - | - | - | - |  | 2oo2 | H2 Buffer Level Pressure Low during Shutdown of Array X | When level is low and array is not in operation, the product valve must be closed |  |  |  | N | [16 empty] | V3.1, 10.05.2024, FR: changed "Array x in operation" to "G0xNHY01KF101/KZ12;XB01"
A |  |  | G0xNHY01KF101/KZ12 | XB01 | - | 0 | - | - | - | -
A |  | 3.1 | H2 Buffer Level Low Low |  | - | 1 | - | - | - | - |  | 2oo2 | H2 Buffer Level Pressure Low during Shutdown of Array Y | When level is low and array is not in operation, the product valve must be closed |  |  |  |  | N | [15 empty] | V3.1, 10.05.2024, FR: changed "Array y in operation" to "G0yNHY01KF101/KZ12;XB01"
A |  |  | G0yNHY01KF101/KZ12 | XB01 | - | 0 | - | - | - | -
A |  | 1.1 | V01NHC10WP002-BP01 | XQ01 | AL 10.0 | ASLL 7.0 | 3.0 | mbar(g) | - | - |  | 1oo2 | H2 Buffer Pressure Low | [14 empty] | S
A |  | 1.1 | V01NHC20CM001-BP01 | XQ01 | L 10.0 | L 7.0 | 3.0 | mbar | - | - |  |  | H2 Buffer Pressure Low | [14 empty] | S
A |  | 1.4 | V01NHC20CM001-BQ01 | XQ01 | AH # | ASHH # | # | ppm |  |  |  | 1oo1 | H2 Buffer H2 Concentration High |  |  | S |  | S | [7 empty] | S | S |  |  |  |  | to be defined project specifically |  |  | V1.4: Line added for switch function at buffertank gas sensor
A |  | 1.4 | V01NHC20CM001-BL04 | XQ01 | AL # | ASLL # | # | % |  |  |  | 1oo1 | HN01 Level Low Low |  |  | S |  | S | [7 empty] | S | S |  |  |  |  | to be defined project specifically |  |  | V1.4: Line added for new level sensor at HN01
A |  | 1.4 | V01NHC20CM001-BL05 | XQ01 | AL # | ASLL # | # | % |  |  |  | 1oo1 | HN02 Level Low Low |  |  | S |  | S | [7 empty] | S | S |  |  |  |  | to be defined project specifically |  |  | V1.4: Line added for new level sensor at HN02
Compressor
A |  | 1.1 | V01NHC30KF001-KF0x | XU01 |  | 0 | - | BOOL | - | - |  | 1oo1 | LP Compressor - Common Fault |  |  | S |  | S | [7 empty] | S | [5 empty] | project specific
A |  | 1.1 | V01NHC31KF001-KF0x | XU01 |  | 0 | - | BOOL | - | - |  | 1oo1 | HP Compressor - Common Fault |  |  | S |  | S | [7 empty] | S | [5 empty] | project specific
Deoxo
A |  | 1.1 | V01NHC40KF001-KF0x | XU01 |  | 0 | - | BOOL | - | - |  | 1oo1 | Common Fault DeOxo |  |  | S | [15 empty] | project specific
UPS
A |  | 1.1 | T01BMA01TB001-KF0x | XU01 |  | 0 | - | BOOL | 15 min | - |  | 1oo1 | Common Fault UPS |  |  | S |  | S | [7 empty] | S
A |  | 3.2 | T01BMA01TB001-KF0y & UPS in battery operation |  |  | 0 | - | BOOL | 2 s | - |  | 1oo1 | Battery low UPS |  |  |  | S | [12 empty] | S | "Battery low" triggers inertization of array(s) on H2 and O2 side, when related UPS supplies emergency power in case of grid failure. Means, the "battery low"-signal must be set in a way that it is still able to inert the supplied array. Inertization status known as long as CPU with power supply. If downstream or other connected H2 systems are not inertized during grid/power failure, positive isolation of array must be ensured to avoid H2 leakages into array. | "Battery low" triggers inertization of array(s) on H2 and O2 side, when related UPS supplies emergency power in case of grid failure. Means, the "battery low"-signal must be set in a way that it is still able to inert all arrays. For multi array plants, dependent on sizing of nitrogen supply system, it might be necessary to inert the arrays after each other. Inertization status known as long as CPU with power supply. If downstream or other connected H2 systems are not inertized during grid/power failure, positive isolation of array must be ensured to avoid H2 leakages into array. If there is no potetial ingress of air into the system (e.g. by ensured N2-blanketed blow off line) it might be discussed, if a N2 purge is necessary (needs to be evaluated during HAZOP based on downstream system design). |  |  | V3.0, BM, JS, FR, 2.11.2023: "Array trip" changed to "Array trip" with inertization. Comment added. V3.2: 8.03.2024 (BM): added: "If there is no potetial of ingress of air into the system (e.g. by ensured N2-blanketed blow off line) it might be discussed, if a N2 purge is necessary (needs be evaluated during HAZOP based on downstream system design)."
Note:
1 | There is no specific constant pressure piston buffer tank in H2 Sakura project downstream of product control valve. Hence customer's contant volume tank to be reffered as buffer tank/volume
2 | ARY1_TRIP_N2_PRG Effect : Array trip with N2 purge command inherently provides command for product valve closure
3 | Tags indicated in Input tags as "K01,T01,A01,V01,QMxx,BPxx" are shown as per Siemens Energy's RDSPP Tagging philosophy, customer's tagging may br different and can be adpated
4 | The cause-and-effect relationships outlined herein are provided solely on the basis of Siemens Energy’s limited experience with complete plant configurations. They are intended for preliminary guidance only and shall not be construed as comprehensive, exhaustive, or finalized from Siemens Energy’s side.
The Customer shall bear full responsibility for conducting detailed investigations, including but not limited to project-specific HAZOP and HAZID studies, to identify any critical causes at the complete plant level that may trigger array safety-related effects.
Any additional causes or effects identified by the Customer may be proposed for inclusion. Incorporation into the safety matrix and associated logic shall be subject to mutual agreement between Siemens Energy and the Customer.
Note on J24: Mahor, Abhishek (ext): Can be in the range of minutes
Note on F28: Mahor, Abhishek (ext): To be aligned with customer based on N2 gas cadre pressures
Note on G28: Mahor, Abhishek (ext): To be aligned with customer based on N2 gas cadre pressures

## BOP - Message only
Operational Messages without Protection Balance of Plant - H2Sakura - has to be adjusted project specifically -
PLS# | Chgd | Input Tag | Signal | Warn | Alarm | Hyst. | Unit | A_DC | A_DG | Func 1 | Func 2 | Cause Description | Comment | Test date/result | Test executed by | Revision history /internal comments
Water Supply System
| 1.4 | A01GCF01CM001-BL01 | XQ01 | AH 95.0 |  |  | % | 10 s |  |  | 1oo1 | Overfill of demin water storage tank
Cooling Water Supply
| 1.1 | A01PAD01WP001-BT01 | XQ01 | AL -20.0 | ASLL -22.0 | 1.0 | °C | 5 min | - |  | 1oo1 | Low Temp. Cooling Water | project specific adjustment required Rectifier cooling must be protected against freezing and condensation by: a) heating during stand still b) autom. instead of manual CV c)add pure Ethylene glycol on Rectifier side (no additives) d) limit time below 0°C
| 1.1 | A01PAD01WP001-BT01 | XQ01 | AH 35 | - | 1.0 | °C | 2 min | - |  | 1oo1 | High Temp. Cooling Water
Trace Heating
| 1.1 | Common Fault |  | 0 | - | - | BOOL | - | - |  | 1oo1 | Common Fault Trace Heating
Low Pressure Buffer Tank
| 1.1 | V01NHC20CM001-BL05 |  | 0 | - | - | BOOL | - | - |  | 1oo1 | H2 Wastewater Separator Level High High
Plant Control
| 1.3 | K01CCA01UH001-BAxx | XU01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Voltage monitoring | Group fault alarm
| 1.3 | K01CCA01UH001-FCxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Circuit breaker feedback | Group fault alarm
| 1.3 | K01CCA01UH001-QAxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Circuit breaker feedback | Group fault alarm
| 1.3 | K01CCA01UH001-TBxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | 24VDC generation feedback | Group fault alarm
| 1.3 | K01CCA01UH001-TFxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | LAN feedback | Group fault alarm

## Ely System - SIS
Safety Functions IEC61511 1 Array - H2 Sakura S --> storing, reset required / speichernd, rücksetzen erforderlich N --> non storing, no reset required / nicht speichernd, rücksetzen nicht erforderlich NP--> non storing purge, reset when purge is finished or canceled / nicht speichernde Spülung, Rücksetzen wenn Spülung beendet oder abgebrochen S* --> storing, reset required / speichernd, rücksetzen erforderlich, not implemented as SIL-rated safety function (IEC61511) N* --> non storing, no reset required / nicht speichernd, rücksetzen erforderlich, not implemented as SIL-rated safety function (IEC61511) NP*--> non storing purge, reset when purge is finished or canceled / nicht speichernde Spülung, Rücksetzen wenn Spülung beendet oder abgebrochen, not implemented as SIL-rate safety function (IEC61511) | [13 empty] | Effect Identifier | CMD_REC1_OFF | CMD_REC2_OFF | CMD_REC3_OFF | CMD_REC4_OFF | CMD_REC1_SCO | CMD_REC2_SCO | CMD_REC3_SCO | CMD_REC4_SCO | CMD_WAT_SUP_CLS | CMD_BLK_N2_PURGE |  | CMD_COMPRESSOR_TRIP | CMD_PRD_VLV_CLS | CMD_N2_PURGE | [6 empty] | CMD_CB1_MV_OPN | CMD_DC+REC1_OFF | CMD_DC+REC2_OFF | CMD_DC+REC3_OFF | CMD_DC+REC4_OFF | CMD_DC-REC1_OFF | CMD_DC-REC3_OFF | CMD_DC-REC2_OFF | CMD_DC-REC4_OFF | CMD_CWS_VLV_CLS | CMD_CWR_VLV_CLS | CMD_REF_PMP_STO |  | GA_H2_S1_NOT_RDY | GA_H2_S2_NOT_RDY | GA_O2_S1_NOT_RDY | GA_O2_S2_NOT_RDY | OPTIONAL: Only for IGBT Rectifier | CMD_CB2_MV_OPN
[14 empty] | Effect Description | Prot. Cmd. Off (E-Stop) - Rect. 1 Customer's scope | Prot. Cmd. Off (E-Stop) - Rect. 2 Customer's scope | Prot. Cmd. Off (E-Stop) - Rect. 3 Customer's scope | Prot. Cmd. Off (E-Stop) - Rect. 4 Customer's scope | Safe Current Off - Rectifier 1 Customer's scope | Safe Current Off - Rectifier 2 Customer's scope | Safe Current Off - Rectifier 3 Customer's scope | Safe Current Off - Rectifier 4 Customer's scope | Demin Supply Valve | Block N2 Purging G01NHX01QN001-KZ03 Low Low N2 Pressure -Safety Purge |  | Compressor Trip | Product Gas Control Valve | Safety N2 Purge (O2&H2) G01NHX01QN001-KZ01 | [5 empty] | Inert required | MV Circuit Breaker1) Customer's scope | Rectifier 1 to 4 DC- & DC+ disconnectors (Scope - To be finalized) | [7 empty] | Cooling Water Supply Valve | Cooling Water Return Valve | Refinement pump |  | Gas Analysis H2 Sensor 1 not ready | Gas Analysis H2 Sensor 2 not ready | Gas Analysis O2 Sensor 1 not ready | Gas Analysis O2 Sensor 2 not ready |  | MV Circuit Breaker1) |  | 1) MV circuit breaker opening to be clarified based on required PFD values for rectifier safety shut down (project specific decision based on HAZOP). As alternative it may be possible to only open the MV circuit breaker if DC disconnectors do not open (subject to confirmation). | 2) IGBT Rectifier does not use "CMD_RECX_OFF" signal. Instead of protection command rect. x off the signal "CMD_RECX_SCO" will be send. |  | V1.4: STO of PolRect changed from S to S* since Contactor of PolRect is already sufficient for SIL2 shut down. V3.2, BM, 7.5.2024: NHC01GT001-QM01 deleted, since not automated anymore V3.3, BM, 8.7.2024: Circuit breaker Identifier renamed from "CMD_CB_MV_OPN" to "CMD_CB1_MV_OPN" V3.3, BM, FR, 16.10.2024: DC disconnectors changed in order to prevent closing and opening of DC disconnectors, when handwheel is plugged 2) IGBT Rectifier does not use "CMD_RECX_OFF" signal. Instead of protection command rect. x off the signal "CMD_RECX_SCO" will be send.
[14 empty] | Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  |  | In general Rect. 3&4 signals are not applicable to IGBT design.
[14 empty] | Output Tag | =G01NHA01TB001-KF01;YB32 | =G01NHA01TB002-KF01;YB32 | =G01NHA01TB003-KF01;YB32 | =G01NHA01TB004-KF01;YB32 | =G01NHA01TB001-KF10;YB32 100 ms delay | =G01NHA01TB002-KF10;YB32 100 ms delay | =G01NHA01TB003-KF10;YB32 100 ms delay | =G01NHA01TB004-KF10;YB32 100 ms delay | =G01NHG01QM001-QM01;YB32 | =G01NHX01QN001-QM21;YB31 | =G01NHX01QN002-QM21;YB32 | =G01NHY01KF001-KZ65;YB31 | =G01NHC01GT001-QN01;YB32 | =G01NHX01QN001-QM11;YB31 | =G01NHX01QN001-QM21;YB31 | =G01NHC01GT001-QN02;YB31 | =G01NHE01GT001-QN01;YB31 | =G01NHX01QN002-QM11;YB32 | =G01NHX01QN002-QM21;YB32 | =G01NHY01KF101/KZ103 | =T01BBA01QA00x-QA01;YW01 | =G01NHA01QZ001-QB01;YB11 =G01NHA01QZ001-QB01;YB12 | =G01NHA01QZ002-QB01;YB11 =G01NHA01QZ002-QB01;YB12 | =G01NHA01QZ003-QB01;YB11 =G01NHA01QZ003-QB01;YB12 | =G01NHA01QZ004-QB01;YB11 =G01NHA01QZ004-QB01;YB12 | =G01NHA01QZ001-QB02;YB11 =G01NHA01QZ001-QB02;YB12 | =G01NHA01QZ002-QB02;YB11 =G01NHA01QZ002-QB02;YB12 | =G01NHA01QZ003-QB02;YB11 =G01NHA01QZ003-QB02;YB12 | =G01NHA01QZ004-QB02;YB11 =G01NHA01QZ004-QB02;YB12 | =G01NHP01WP001-QM02;YB32 | =G01NHP01WP001-QM08;YB32 | =G01NHH01HP001-GP01; YB21 |  | =G01NHC01BQ001-KZ41; XM01 | =G01NHC01BQ001-KZ42; XM01 | =G01NHE01BQ001-KZ41; XM01 | =G01NHE01BQ001-KZ42; XM01 |  | =T01BBA01QA00x-QA02;YW01
[14 empty] | Action | off | off | off | off | off | off | off | off | close | close | close | on | close | open | open | open | open | open | open | on | open | off (not open or close) | off (not open or close) | off (not open or close) | off (not open or close) | off (not open or close) | off (not open or close) | off (not open or close) | off (not open or close) | close | close | off |  | not ready | not ready | not ready | not ready |  | open |  |  |  |  | Revision history /internal comments
Customer Revision | Cause Identifier | Chgd | Input Tag | Signal | Warn | Safety Limit | Hyst. | Unit | Delay | Func 1 | Func 3 | Cause Description | Comment | [33 empty] | Response Time | [6 empty] | MOS | Comments, Causes / Kommentare, Ursachen | Test date/result | Test executed by
System Control
| BPCS_COM_FLT | GnyNHY01KF002-TF06 | GnyNHY01KF002-TF06 | XM01 | - | 1 | - | BOOL | - |  | 1oo1 | BPCS Communication Fault | 1= Fault of Lifebit Monitoring (from BPCS) |  | S* | S* | S* | S* | S* | S* | S* | S* |  |  |  | S* | S* | NP* | NP* | NP* | NP* | NP* | NP* | NP* | [19 empty] | no | On communication fault to BPCS: Rectifier Safe Off, Demin Supply Shufoff and Safety N2 Purge is caused in SIS, because DC disconnectors can not be opened and pressure hold with N2 does not work. The SIF Effects, which are caused in the SIS, shall be considered as active (or bad signal state) in the BPCS logic to react accordingly. |  |  |  | N.OK Not implemented 21.04.2026
| TRIG_N2_PRG_MAINT | GnyNHY01KF101/KZ86 | GnyNHY01KF101/KZ86 |  | - | 1 | - | BOOL | - |  | 1oo1 | Trigger Safety N2 Purge for Maintenance Mode | 1= Trigger Safety N2 Purge (from BPCS) | [13 empty] | S* | NP* | NP* | NP* | NP* | NP* | NP* | NP* | [19 empty] | no | When "Activating Maintenance" of the Electroylsis System with option "Gas System = Off", the Safety N2 Purge shall be activated from the operational step sequence to enable a coordinated shutdown. As the step sequence will shut down the pressure hold function and the gas analytics, the Safety N2 Purge would be activated anyway. |  |  |  | Checked OK 21-04-2026 PD
Balance of Plant (BoP)
| ARY_TRIP | 3.3 | G01NHY01KF002-KZ01 | XV01 | - | 0 | - | BOOL | - |  | 1oo1 | Array - Safety Trip (from BoP) | via hardwired failsafe input |  | N* | N* | N* | N* | [7 empty] | N* | N* | [19 empty] | 1s (Rectifier) | [6 empty] | no | project specific, if trip of rectifiers without N2 Purge is required If reset is required, this shall be implemented in the higher level system | 24.04.2025 implemented change | F.Reinhart | V1.4 (FR): added signal exchange between BoP and Array V2.0: 2023-08-16 (JS, DW, BM): alles in S*, da aktuell kein Bedarf für diese Schaltung V3.2, BM, 2024-05-15: KF001 changed to KF002 V3.3, FR+BM+JS, 2025-02-13: removed trip of MV CB, because inconsistent with other trips and not required V3.3, BM+FR, 2025-04-22: changed S* to N*, because reset shall be done in higher level system | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect
| ARY_TRIP_N2_PRG | 3.3 | G01NHY01KF002-KZ03 | XV01 | - | 0 | - | BOOL | - |  | 1oo1 | Array - Safety Trip with N2 Purge (from BoP) | via hardwired failsafe input |  | N* | N* | N* | N* | [7 empty] | N* | N* | NP* | NP* | NP* | NP* | NP* | NP* | NP* | [12 empty] | 1s (Rectifier) | [6 empty] | no | During N2 Purge the Rectifiers must also be shutdown to reach a safe inerted state. Only failsafe processing. SIL not defined for e-stop/gas alarm/fire. If reset is required, this shall be implemented in the higher level system | 24.04.2025 implemented change | F.Reinhart | V1.4 (FR): added signal exchange between BoP and Array V2.0: 2023-08-16: SIL ist mit allen genannten Aktoren nicht möglich. Kein SIL definiert für e-stop/gas alarm/feuer. Begründung für Gasalarm: Gassensoren sind kein primärer Ex-Schutz, sondern nur eine Zusatzmaßmahme und deshalb kein SIL. inter required in NP* not S* V3.1, V2.1(FR, 01.02.2024): CMD_PRD_VLV_CLS changed from NP* to S* to keep closed after purge V3.2, 2024-04-05, BM: Pol. Rectifier in description deleted. V3.2, BM, 2024-05-15: KF001 changed to KF002 V3.3, BM+FR, 2025-04-22: changed S* to N*, because reset shall be done in higher level system | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect
| ARY_TRIP_N2_BLK | 3.3 | G01NHY01KF002-KZ04 | XV01 | - | 0 | - | BOOL | - |  | 1oo1 | Array - Safety Trip and Block N2 Purge (from BoP) | via hardwired failsafe input |  | N* | N* | N* | N* | [5 empty] | N* | N* | N* | N* | [19 empty] | 1s (Rectifier) | [6 empty] | no | project specific If reset is required, this shall be implemented in the higher level system | 24.04.2025 implemented change | F.Reinhart | V1.4 (FR): added signal exchange between BoP and Array 2023-08-16: Gas qualität als Abschaltkriterium im SIS BoP Teil wurde gestrichen, damit ist diese Zeile vorerst nicht notwendig. V3.2, BM, 2024-05-15: KF001 changed to KF002 V3.3, BM+FR, 2025-04-22: changed S* to N*, because reset shall be done in higher level system | Checked OK 10-04-2026 PD
| ARY_PRD_VLV_CLS | 3.3 | G01NHY01KF002-KZ05 | XV01 | - | 0 | - | BOOL | - |  | 1oo1 | Close Product Valve (from BoP) | via hardwired failsafe input | [13 empty] | N* | [19 empty] | 1s (Rectifier) | [6 empty] | no | project specific, if separate closure of product valve is required. If required project specifically, max. SIL2 is possible. If reset is required, this shall be implemented in the higher level system | 24.04.2025 implemented change | F.Reinhart | V1.4 (FR): added signal exchange between BoP and Array V2.0: 2023-08-16 (JS, DW, BM): aktuell keine Anforderung in SIL2, wäre aber möglich. V3.2, BM, 2024-05-15: KF001 changed to KF002 V3.3, BM+FR, 2025-04-22: changed S* to N*, because reset shall be done in higher level system | Checked OK 10-04-2026 PD
Gas Separation
| LVL_SEP_H2_HL1 | 2.0 | G01NHC01BL001-BL01 | XQ01 | AH 40.0 | AZHH 47.0 | 1.0 | cm | - |  | 1oo1 | Level - Gas separator H2 - High limit 1 |  |  | S* | S* | S* | S* | S | S | S | S | S |  |  | S* | S* | [19 empty] | 1s (Rectifier) | [6 empty] | no | - Level Control - level shift O2/H2 sides | 25.04.2025 implemented change | F. Reinhart | V2.0 29.08.2023: (JS, BM, RW, GL, FH): MV circuit breaker not necessary | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect SIF Cause Level Graphics S* missing in CMD_PRD_VLV_CLS and CMD_COMPRESSOR_TRIP
| LVL_SEP_H2_HL2 | 3.2 |  | XQ01 |  | AZHHH 70.0 | 1.0 | cm | - |  | 1oo1 | Level - Gas separator H2 - High limit 2 | Cooler break through: alarm message must request manual depressurization of cooling water system | [30 empty] | S | S | [8 empty] | no | - project specific - operator receives request on HMI to depressurize the cw system on array side. - G0yNHP01WP001-QM45: only manual depressurization of by manual valve (local) or optionally by manual triggered on/off valve (remote) of cooling system, because trip becomes also active on CPU stop, electrical fault or fault of instrument air - otherwise unintended release of cooling water (incl. glycol) can be caused - response time < 24 h (5 mm² hole, 4 barg) | 25.04.2025 implemented change | F. Reinhart | V1.3: isolation of cooling water system added at 70 cm level V3.2, 2024-04-05, BM: ">" changed to "<" FR, BM, JS, 2024-05-22: change signal =G0xNHY01KF001-KZ51 which was sent to to plant control to direct actuation of cw isolatiion valves. Before this action was shown in BoP SIS part. | Checked OK 10-04-2026 PD
| LVL_SEP_H2_LL1 | 3.3 | G01NHC01BL001-BL01 | XQ01 | AL (Note 1) | AZLL (Note 1) | 1.0 | cm | 3 min |  | 1oo1 | Level - Gas separator H2 - Low limit 1 |  |  | S* | S* | S* | S* | S | S | S | S |  |  |  | S* | S* | [19 empty] | 1s (Rectifier) | [6 empty] | no | Note 1: variable level limits based on independent rectifier current (=G01NHA01BZ00x-BC02), min level 5 cm. failure cases: - Level Control - low or no flow from demin supply | 25.04.2025 implemented change | F. Reinhart | V2.0: 2023-08-25 (JS, DW, BM): nur Hauptgleichrichter und PolGr in S, denn Fehlfall: keine Nachspeisung. Durch Abschalten des Hauptgleichrichter wird der Wasserverbrauch unterbunden. N2 Spülung ist nicht Teil des SIF, da keine großen Wasserleckagen angenommen werden, die nicht durch die Nachspeisung ausgeglichen werden können. - PolGr verbraucht max. 1,2 l/h @ 16A je Modulgruppe (4 Module). - varibler Grenzwert nötig (see tab " var. SIS level (intern)) Bei Reglerfehler im Abblaseventil und Levelverschiebung müssen zusätzlich die Abblaseventile sicherheitsgerichtet ??? geöffnet werden, um einen Abbau des Differenzdruckes zu gewährleisten. siehe hierzu nächst niederigeren Levelgrenzwert V2.0 29.08.2023: (JS, BM, RW, GL, FH): MV circuit breaker not necessary V3.3, 25.04.2025, FR+BM: variable limit was adjusted (see tab var. level limits) | Checked OK 10-04-2026 PD
| LVL_SEP_H2_LL2 | 3.1 | G01NHC01BL001-BL01 | XQ01 |  | AZLLL 1.0 4.0 |  | cm | - |  | 1oo1 | Level - Gas separator H2 - Low limit 2 |  |  | S* | S* | S* | S* | S | S | S | S |  |  |  | S* | S* | NP* | NP* | NP | NP | NP* | NP* | NP* | [12 empty] | 1s (Rectifier) | [6 empty] | no | - Critical and sudden level shifts O2/H2 sides | 25.04.2025 implemented change | F. Reinhart | V2.0: 2023-08-16 (JS, DW, BM): fester Grenzwert & unverzögert, um plötzliche Levelverschiebungen abzufangen. V2.0: 2023-08-23 (JS, GL, FR, FH, RW, BM): Fehlerfall: O2 vent valve öffnet nicht bzw. schließt fehlerhaft V3.0: 14.11.2023, JS: MV nicht notwendig, da PFD von neuem modularen Gleichrichter ausreichend gut. V3.1, V2.1 (FR, 01.02.2024): CMD_PRD_VLV_CLS changed from NP* to S* to keep closed after purge | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect
| LVL_SEP_O2_HL1 | 1.1 | G01NHE01BL001-BL01 | XQ01 | AH 40.0 | AZHH 47.0 | 1.0 | cm | - |  | 1oo1 | Level - Gas separator O2 - High limit 1 |  |  | S* | S* | S* | S* | S | S | S | S | S |  |  | S* | S* | [19 empty] | 1s (Rectifier) | [6 empty] | no | - Level Control - level shift O2/H2 sides | 25.04.2025 implemented change | F. Reinhart | V2.0: 2023-08-31 (JS, BM): MV circuit braker deleted. | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect
| LVL_SEP_O2_HL2 | 3.2 |  | XQ01 |  | AZHHH 70.0 | 1.0 | cm | - |  | 1oo1 | Level - Gas separator O2 - High limit 2 | Cooler break through: alarm message must request manual depressurization of cooling water system | [30 empty] | S | S | [8 empty] | no | - project specific - operator receives request on HMI to depressurize the cw system on array side. - G0yNHP01WP001-QM45: only manual depressurization of by manual valve (local) or optionally by manual triggered on/off valve (remote) of cooling system, because trip becomes also active on CPU stop, electrical fault or fault of instrument air - otherwise unintended release of cooling water (incl. glycol) can be caused - response time < 24 h (5 mm² hole, 4 barg) | 25.04.2025 implemented change | F. Reinhart | V1.3: isolation of cooling water system added at 70 cm level V3.2, 2024-04-05, BM: ">" changed to "<" FR, BM, JS, 2024-05-22: change signal =G0xNHY01KF001-KZ51 which was sent to to plant control to direct actuation of cw isolatiion valves. Before this action was shown in BoP SIS part. | Checked OK 10-04-2026 PD
| LVL_SEP_O2_LL1 | 3.3 | G01NHE01BL001-BL01 | XQ01 | AL (Note 1) | AZLL (Note 1) | 1.0 | cm | 3 min |  | 1oo1 | Level - Gas separator O2 - Low limit 1 |  |  | S* | S* | S* | S* | S | S | S | S |  |  |  | S* | S* | [19 empty] | 1s (Rectifier) | [6 empty] | no | Note 1: variable level limits based on independent rectifier current (=G01NHA01BZ00x-BC02), min level 5 cm. failure cases: - Level Control - low or no flow from demin supply | 25.04.2025 implemented change | F. Reinhart | V2.0: 2023-08-25 (JS, DW, BM): nur Hauptgleichrichter und PolGr in S, denn Fehlfall: keine Nachspeisung. Durch Abschalten des Hauptgleichrichter wird der Wasserverbrauch unterbunden. N2 Spülung ist nicht Teil des SIF, da keine großen Wasserleckagen angenommen werden, die nicht durch die Nachspeisung ausgeglichen werden können. - PolGr verbraucht max. 1,2 l/h @ 16A je Modulgruppe (4 Module). - varibler Grenzwert nötig (see tab " var. SIS level (intern)) Bei Reglerfehler im Abblaseventil und Levelverschiebung müssen zusätzlich die Abblaseventile sicherheitsgerichtet ??? geöffnet werden, um einen Abbau des Differenzdruckes zu gewährleisten. siehe hierzu nächst niederigeren Levelgrenzwert V2.0 29.08.2023: (JS, BM, RW, GL, FH): MV circuit breaker not necessary V3.3, 25.04.2025, FR+BM: variable limit was adjusted (see tab var. level limits) | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect
| LVL_SEP_O2_LL2 | 3.1 | G01NHE01BL001-BL01 | XQ01 |  | AZLLL 1.0 4.0 |  | cm | - |  | 1oo1 | Level - Gas separator O2 - Low limit 2 |  |  | S* | S* | S* | S* | S | S | S | S |  |  |  | S* | S* | NP* | NP* | NP | NP | NP* | NP* | NP* | [12 empty] | 1s (Rectifier) | [6 empty] | no | - Critical and sudden level shifts O2/H2 sides | 25.04.2025 implemented change | F. Reinhart | 2023-08-16: Level bei 1 cm fällt weg. Die Abschaltungen für PolGr und die N2 Spülung werden bei Level 5 cm berücksichtigt. V2.0 2023-08-18: varibler Grenzwert nötig (see tab " var. SIS level (intern)) V3.0: 14.11.2023, JS: MV nicht notwendig, da PFD von neuem modularen Gleichrichter ausreichend gut. V3.1, V2.1 (FR, 01.02.2024): CMD_PRD_VLV_CLS changed from NP* to S* to keep closed after purge | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect
| PRS_SEP_H2_HL | 3.0 | G01NHC01HP001-BP01 | XQ01 | AH 140.0 | AZHH 155.0 | 5.0 | mbar(g) | - |  | 1oo1 | Pressure - Gas separator H2 - High limit |  |  | S* | S* | S* | S* | S | S | S | S |  | S* | S* | S* | S | [19 empty] | 1s | [6 empty] | no | - failure in Pressure Control - when pressure limit is exceeded and falls again below the limit the lance shall be purged with N2 (f no N2 blanketing). This shall cover a potential blow off scenario over PSV and flush out residual H2. | 25.04.2025 implemented change | F. Reinhart | V1.4 (FR): changed Hyst from 2.0 to 5.0 for consistency with operational sensor V2.0: 2023-08-29: (FR, JS, RW, BM): Produktgasventil soll in S geschlossen, um ein Entleeren des Puffertanks zu verhindern, wenn NHC01GT001-QM01 nicht geöffnet ist bzw. fehlerhaft schließt. MV circuit braker. V3.0, BM, JS, 30.10.2023: aufgrund der Schnelle des Druckanstiegs im Fehlerfall, kann eine Druck Hoch Abschaltung kein Sicherheitsventil ersetzen. Es soll lediglich das dauerhafte Abblasen verhindern. V3.0, BM, 06.11.2023: N2 Ventile sollen blockiert werden, um Druck nicht weiter steigen zu lassen (z.B. PolGr Betrieb mit N2 Spülung). S* ausreichend, zusätzlich PSV vorhanden. Eine sicherheitsgerichtete Spülung darf dadurch aber nicht blockiert werden. V3.2, BM, RW, 24.05.2024: S für Produktgasventil bei zu hohem Druck auf O2 Seite entfernt, da dort kein Entleeren des Puffertanks möglich ist und NHE01GT001-QM01 nicht existiert. | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect
| PRS_SEP_O2_HL | 3.2 | G01NHE01HP001-BP01 | XQ01 | AH 140.0 | AZHH 155.0 | 5.0 | mbar(g) | - |  | 1oo1 | Pressure - Gas separator O2 - High limit |  |  | S* | S* | S* | S* | S | S | S | S |  | S* | S* | S* | S* | [19 empty] | 1s | [6 empty] | no |  | 25.04.2025 implemented change | F. Reinhart |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect , S* missing in CMD_PRD_VALV
| PRS_SEP_H2_LL | 3.3 | G01NHC01HP001-BP01 | XQ01 | AL 15.0 | AZLL 7.0 | 5.0 | mbar(g) | 30 s |  | 1oo1 | Pressure - Gas separator H2 - Low limit |  |  | S* | S* | S* | S* | S* | S* | S* | S* |  |  |  | S* | S | NP | NP | NP | NP* | NP* | NP* | NP* | [12 empty] | 1s | [6 empty] | no | - pressure control, cooling down (only during standby), blow off valve open. - ingress of air possible, inertization required rect. and polrect are interlocked and not part of SIL protection loop. Operator must check, if additional N2 purge is necessary before start of rectifiers, therfore inert required in "NP". | 25.04.2025 implemented change | F. Reinhart | V2.0: 2023-08-11: NHE01GT001-QN01 muss nicht in S sein, da nur die H2 Seite gespült werden muss. Wenn das H2 vent valve fehlerhaft geöffnet ist (ohne N2 Spülung der H2 Abblaselanze), dann wird einmalig gespült, aber das H2 vent valve bleibt fehlerhaft offen, wodurch wieder Luft in die Anlage kommen kann. Deshalb muss die Anlage/Gleichrichter verriegelt bleiben und ggf. muss nochmal gespült werden vor dem Anfahren. Inert required in S und nicht in NP. V2.0: 2023-08-31 (JS, BM): MV circuit braker deleted. V3.1, V2.1 (FR, 01.02.2024): CMD_PRD_VLV_CLS changed from NP* to S* to keep closed after purge V3.3, BM, FR, JS: Increase of trip value from 0 to 7 mbarg to cover measurement uncertainty. warning also increased from 10 to 15 mbarg. | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect
Module Temperatures
| TMP_SG1_H2_HL | 3.3 | G01NHB01EQ001-BT02 | XQ01 | AH 63.0 | AZHH 65.0 | 1.0 | °C | - |  | 1oo12 | Temperature - SG 1 H2 - High limit | cooler outlet H2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no | Cooling control, If GDL is changed to other type the temperature difference beteewn in- and outlet of stack can increase. Then, limit set point must be check and reconfirmed. | 05.03.2025 Implemented change | P,Kumar | V1.3: Warnung von 68 auf 60°C und trip von 70 auf 65 reduziert (Hintergrund: SGU BASF) INTERN: Modul TS 75°C auf 80 geändert. Für 30 min auch 85°C erlaubt. Messfehler abgeschätzt mit 3,2 K (höher als Messunsicherheit des Sensors, aber inkl. Einflüsse in Kabel und Leittechnik, Vorschlag BASF). max. Spreizung über Modul: EoL, 1,56 A/cm² -> 10,1 K Erwärmung während Reaktionszeit + Ansprechzeit Sensor: 2,4 K 85°C - 3,2K -10K-2,4 K = 69,4°C -> gewählt 68°C Falls die Spreizung geändert wird (anderer Modultyp: MLH GDL), muss auch der Grenzwert angepasst werden. MLH-GDL: 85°C - 3,2K -13 K-2,4 K = 66,4°C -> zu wählen: Trip bei 65°C V2.0: 2023-08-31 (JS, BM): MV circuit braker deleted. V3.3, BM+FR, 2025-01-15: Warning limit was increased from 60 to 63 °C, because at partload with BoL stacks, the cooling is nearly not required and with an operating temperature of 60 °C and a slight overshoot of the Temperature Control it can happen that the temperature rises above 60 °C. | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG1_O2_HL | 3.3 | G01NHB01EQ001-BT03 | XQ01 | AH 63.0 | AZHH 65.0 | 1.0 | °C | - |  |  | Temperature - SG 1 O2 - High limit | cooler outlet O2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG2_H2_HL | 3.3 | G01NHB02EQ001-BT02 | XQ01 | AH 63.0 | AZHH 65.0 | 1.0 | °C | - |  | 1oo12 | Temperature - SG 2 H2 - High limit | cooler outlet H2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG2_O2_HL | 3.3 | G01NHB02EQ001-BT03 | XQ01 | AH 63.0 | AZHH 65.0 | 1.0 | °C | - |  |  | Temperature - SG 2 O2 - High limit | cooler outlet O2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG3_H2_HL | 3.3 | G01NHB03EQ001-BT02 | XQ01 | AH 63.0 | AZHH 65.0 | 1.0 | °C | - |  | 1oo12 | Temperature - SG 3 H2 - High limit | cooler outlet H2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG3_O2_HL | 3.3 | G01NHB03EQ001-BT03 | XQ01 | AH 63.0 | AZHH 65.0 | 1.0 | °C | - |  |  | Temperature - SG 3 O2 - High limit | cooler outlet O2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG4_H2_HL | 3.3 | G01NHB04EQ001-BT02 | XQ01 | AH 63.0 | AZHH 65.0 | 1.0 | °C | - |  | 1oo12 | Temperature - SG 4 H2 - High limit | cooler outlet H2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG4_O2_HL | 3.3 | G01NHB04EQ001-BT03 | XQ01 | AH 63.0 | AZHH 65.0 | 1.0 | °C | - |  |  | Temperature - SG 4 O2 - High limit | cooler outlet O2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG5_H2_HL | 3.3 | G01NHB05EQ001-BT02 | XQ01 | AH 63.0 | AZHH 65.0 | 1.0 | °C | - |  | 1oo12 | Temperature - SG 5 H2 - High limit | cooler outlet H2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG5_O2_HL | 3.3 | G01NHB05EQ001-BT03 | XQ01 | AH 63.0 | AZHH 65.0 | 1.0 | °C | - |  |  | Temperature - SG 5 O2 - High limit | cooler outlet O2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG6_H2_HL | 3.3 | G01NHB06EQ001-BT02 | XQ01 | AH 63.0 | AZHH 65.0 | 1.0 | °C | - |  | 1oo12 | Temperature - SG 6 H2 - High limit | cooler outlet H2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG6_O2_HL | 3.3 | G01NHB06EQ001-BT03 | XQ01 | AH 63.0 | AZHH 65.0 | 1.0 | °C | - |  |  | Temperature - SG 6 O2 - High limit | cooler outlet O2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG1_H2_LL | 3.3 | G01NHB01EQ001-BT02 | XQ01 | AL 5.0 | AZLL 2.0 | 1.0 | °C | 10 min |  | 1oo12 | Temperature - SG 1 H2 - Low limit | cooler outlet H2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no | Project specific: Mainly dependent on recooling system and plant location. Especially relevant in multi array plant with water/glycol mixtures (< 0°C). | 05.03.2025 Implemented change | P,Kumar | V1.3: Kommentar hinzugefügt V2.0: 2023-08-31 (JS, BM): MV circuit braker deleted. V3.3, BM, JS, FR, 21.10.2024: "S" for SCO deleted, since no SIL requirement. | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG1_O2_LL | 3.3 | G01NHB01EQ001-BT03 | XQ01 | AL 5.0 | AZLL 2.0 | 1.0 | °C | 10 min |  |  | Temperature - SG 1 O2 - Low limit | cooler outlet O2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG2_H2_LL | 3.3 | G01NHB02EQ001-BT02 | XQ01 | AL 5.0 | AZLL 2.0 | 1.0 | °C | 10 min |  | 1oo12 | Temperature - SG 2 H2 - Low limit | cooler outlet H2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG2_O2_LL | 3.3 | G01NHB02EQ001-BT03 | XQ01 | AL 5.0 | AZLL 2.0 | 1.0 | °C | 10 min |  |  | Temperature - SG 2 O2 - Low limit | cooler outlet O2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG3_H2_LL | 3.3 | G01NHB03EQ001-BT02 | XQ01 | AL 5.0 | AZLL 2.0 | 1.0 | °C | 10 min |  | 1oo12 | Temperature - SG 3 H2 - Low limit | cooler outlet H2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG3_O2_LL | 3.3 | G01NHB03EQ001-BT03 | XQ01 | AL 5.0 | AZLL 2.0 | 1.0 | °C | 10 min |  |  | Temperature - SG 3 O2 - Low limit | cooler outlet O2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG4_H2_LL | 3.3 | G01NHB04EQ001-BT02 | XQ01 | AL 5.0 | AZLL 2.0 | 1.0 | °C | 10 min |  | 1oo12 | Temperature - SG 4 H2 - Low limit | cooler outlet H2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG4_O2_LL | 3.3 | G01NHB04EQ001-BT03 | XQ01 | AL 5.0 | AZLL 2.0 | 1.0 | °C | 10 min |  |  | Temperature - SG 4 O2 - Low limit | cooler outlet O2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG5_H2_LL | 3.3 | G01NHB05EQ001-BT02 | XQ01 | AL 5.0 | AZLL 2.0 | 1.0 | °C | 10 min |  | 1oo12 | Temperature - SG 5 H2 - Low limit | cooler outlet H2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG5_O2_LL | 3.3 | G01NHB05EQ001-BT03 | XQ01 | AL 5.0 | AZLL 2.0 | 1.0 | °C | 10 min |  |  | Temperature - SG 5 O2 - Low limit | cooler outlet O2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG6_H2_LL | 3.3 | G01NHB06EQ001-BT02 | XQ01 | AL 5.0 | AZLL 2.0 | 1.0 | °C | 10 min |  | 1oo12 | Temperature - SG 6 H2 - Low limit | cooler outlet H2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| TMP_SG6_O2_LL | 3.3 | G01NHB06EQ001-BT03 | XQ01 | AL 5.0 | AZLL 2.0 | 1.0 | °C | 10 min |  |  | Temperature - SG 6 O2 - Low limit | cooler outlet O2 side |  | S* | S* | S* | S* | S | S | S | S | [24 empty] | 10s | [6 empty] | no |  |  |  |  | Checked OK 10-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
| Gas Analytic H2 side - G01NHC01BQ001-BQ01(discont.) | [53 empty] | shutoff source when high or unknown/invalid, inertization after high
| CCN_GA_H2_HL1 | 3.3 | G01NHC01BQ001-BQ01 | XQ01 |  | AZHHH 7000 | 1000 | ppm | - |  | 1oo2* | Concentration - Gas analytic H2 - High limit for Deoxo | Concentration of sensor 1 | [33 empty] | 2s | [6 empty] | no | Deoxo shall be protected by closing the product gas valve until gas quality is good enough again. Limit is not fixed and must be adopted depending on deoxo design. If no deoxo is installed downstream, the closing of product gas valve is not mandatory. It may be necessary to change this value to other project specific restrictions/downstream systems.Values below 7.000 ppm are not considered as practical and would limit operation. *One sensor fault (GA_H2_S1_NOT_RDY or GA_H2_S2_NOT_RDY): Bypass of affected Sensor due to faulty sensor and logic is degraded from 1oo2 to 1oo1. After a delay of 72 h the SIF is tripped. In case of two sensor faults (GA_H2_S1_NOT_RDY and GA_H2_S2_NOT_RDY) the SIF is tripped without delay. | 25.04.2025 implemented change | F. Reinhart | V1.4: Failure cause: fault in refinment distribution. Value relevant for deoxo protection . See decision in BASF project. Safety oriented shut down of refinement pump necessary. 26.07.2023 STO of PolRect in S* since AC circuit breaker is sufficient for SIL2 V2.0 2023-08-11: failure in refinement distribution (only possible during electrolyer standby) covered by safety oriented pump shutdown. V3.2, 2024-07-02, BM, JS, RW: Negations of bad signal, sensor fault and calibration mode deleted since these are covered by "S1 / S2 not ready". V3.3, 2025-04-23, BM+FR+JS: moved trip of Refinement Pump to from CCN_GA_H2_HL1 to CCN_GA_H2_HL2, because first limit is reserved for Deoxo | Checked OK 13-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect | bar: S* S* to S* S
|  |  | G01NHC01BQ001-BQ02 | XQ01 |  | AZHHH 7000 | 1000 | ppm | - |  |  |  | Concentration of sensor 2 | [45 empty] | Checked OK 13-04-2026 PD Graphics NOK SIF CASUE Effect matrix need to add compressor Trip Effect
| CCN_GA_H2_HL2 | 3.3 | G01NHC01BQ001-BQ01 | XQ01 | - | AZHHHH 17000 | 1000 | ppm | - |  | 1oo2* | Concentration - Gas analytic H2 - High limit for Electrolyzer | Concentration of sensor 1 |  | S* | S* | S* | S* | S | S | S | S |  |  |  | S* | S* | NP* | NP* | NP* | NP* | NP* | NP* | NP* | [11 empty] | S | 10s | [6 empty] | no | Not valid for downstream systems (Customer/DeOxo), Limit reduced to 17000 ppm due to measurement deviation/offset of 3000 ppm. Pump in refinement is shut down in order to prevent foreign gas increase based on faulty water distrbution. *One sensor fault (GA_H2_S1_NOT_RDY or GA_H2_S2_NOT_RDY): Bypass of affected Sensor due to faulty sensor and logic is degraded from 1oo2 to 1oo1. After a delay of 72 h the SIF is tripped. In case of two sensor faults (GA_H2_S1_NOT_RDY and GA_H2_S2_NOT_RDY) the SIF is tripped without delay. | 25.04.2025 implemented change | F. Reinhart | V1.3: Warning changed V1.4: Warning not required because already implemented in operational logic (same sensor); Deoxo is not covered by this limit. 22.05.2023: PolGr werden schon früher abgeschaltet um SIL Qualität für diesen Kreis erfüllen zu können Produktgasventil von S auf S* geändert, da schon bei niedrigeren Grenzwerten geschlossen V2.0 2023-08-11: failure in module (not likely) or slow degradation (also unlikely). More lilkely is high foreign gas concetration on O2 side. Nevertheless, rect. and polrect remain in S. V2.0: 2023-08-31 (JS, BM): MV circuit braker deleted. V3.1, V2.1 (FR, 01.02.2024): CMD_PRD_VLV_CLS changed from NP* to S* to keep closed after purge V3.2, 2024-07-02, BM, JS, RW: Negations of bad signal, sensor fault and calibration mode deleted since these are covered by "S1 / S2 not ready". V3.3, 2025-04-23, BM+FR+JS: moved trip of Refinement Pump to from CCN_GA_H2_HL1 to CCN_GA_H2_HL2, because first limit is reserved for Deoxo | Checked OK 20-04-2026 PD
|  |  | G01NHC01BQ001-BQ02 | XQ01 | - | AZHHHH 17000 | 1000 | ppm | - |  |  |  | Concentration of sensor 2 | [45 empty] | Checked OK 20-04-2026 PD | bar: S* S to S* NP*
| GA_H2_S1_NOT_RDY | 3.3 | G01NHC01BQ001-QM27 | XB02 | - | 0 | - | Bool | - |  | 1oo6 | Gas analytic H2 - Sensor 1 not ready | 0= cal. valve in calibration pos. | [33 empty] | 10s | N* | [5 empty] | no | - Sensor Drift (KZ31) is Delta between saved Gas Concentration during Validation (KZ10/KZ20) and saved Setpoint [SP] of Validation Gas (KZ71) - the Setpoint of the Validation Gas is also saved and only updated when a new Gas Concentration for Validation Gas is saved (i.e. changing the Setpoint is possible without influencing the last evaluation) - warning/alarm message for calibration request on sensor drift - min flow at L 10.0 l/h * limit values depend on Setpoint [SP] of Validation Gas, e.g. for validation gas of 500 ppm the alarm values should be ASLL -100 ppm (-20% of 500 ppm) and ASHH 1500 ppm (300% of 500 ppm) | 13.05.2025 implemented change | F.Reinhart | V1.3: Warning changed double failure not considered (no valid sensor signal available + high foreign gas concentration) 22.05.2023: PolGr führt auf H2 Seite im Normalbetrieb nicht zu einer Fremdgaserhöhung 25.05.2023: Produktgasventil geschlossen, wenn Gasanalyitc aus ist, um Systeme stromab zu schützen. Spülung wieder eingefügt, damit Refinement nicht abgeschaltet werden muss (Problematisch: O2 in H2 bei Refinmentbetrieb) V2.0 2023-08-16: Shut down of rectifier/polrect/N2 purge only in S* V2.0: 2023-08-31 (JS, BM): MV circuit braker deleted. V3.1, V2.1 (FR, 01.02.2024): CMD_PRD_VLV_CLS changed from NP* to S* to keep closed after purge V3.2, 2024-07-01, BM, RW, JS, FR: GA not ready split up in S1 and S2. Actors (rectifier STO & N2 purge deleted. instead "GA Not Ready"; Sensor drift included from operational part V3.3, 2025-05-13, FR+RW: the limit values are dynamic and depend on the Setpoint of the Validation Gas; Sensor Drift and Setpoint are saved until new measurement of validation gas | Checked OK 20-04-2026 PD
|  |  | G01NHC01BQ001-BF01 | XG02 | - | 0 | - | Bool | 10 s |  |  |  | 0= low flow of sensor 1
|  |  | G01NHC01BQ001-BQ01 | XQ01_BAD | - | 1 | - | Bool | - |  |  |  | 1= bad signal of sensor 1
|  |  | G01NHC01BQ001-BQ01 | XM01 | - | 0 | - | Bool | - |  |  |  | 0= fault of gas sensor 1
|  |  | G01NHC01BQ001-KZ31 | XQ01 | AL -15% SP* | ASLL -20% SP* | - | Delta ppmV | 1 s |  |  |  | sensor drift low of gas sensor 1 (from BPCS)
|  |  | G01NHC01BQ001-KZ31 | XQ01 | AH 200% SP* | ASHH 300% SP* | - | Delta ppmV | 1 s |  |  |  | sensor drift high of gas sensor 1 (from BPCS)
| GA_H2_S2_NOT_RDY | 3.3 | G01NHC01BQ001-QM23 | XB02 | - | 0 | - | Bool | - |  | 1oo6 | Gas analytic H2 - Sensor 2 not ready | 0= cal. valve in calibration pos. | [35 empty] | N* |  |  |  |  | no |  | 13.05.2025 implemented change | F.Reinhart |  | Checked OK 20-04-2026 PD
|  |  | G01NHC01BQ001-BF02 | XG02 | - | 0 | - | Bool | 10 s |  |  |  | 0= low flow of sensor 2
|  |  | G01NHC01BQ001-BQ02 | XQ01_BAD | - | 1 | - | Bool | - |  |  |  | 1= bad signal of sensor 2
|  |  | G01NHC01BQ001-BQ02 | XM01 | - | 0 | - | Bool | - |  |  |  | 0= fault of gas sensor 2
|  |  | G01NHC01BQ001-KZ32 | XQ01 | AL -15% SP* | ASLL -20% SP* | - | Delta ppmV | 1 s |  |  |  | sensor drift low of gas sensor 2 (from BPCS)
|  |  | G01NHC01BQ001-KZ32 | XQ01 | AH 200% SP* | ASHH 300% SP* | - | Delta ppmV | 1 s |  |  |  | sensor drift high of gas sensor 2 (from BPCS)
| GA_H2_DIL_FLW | 2.0 | G01NHC01BQ001-QM11 | XB02 | - | 0 | - | BOOL | 20 s |  | 2oo8 | Gasanalytic H2 - Dilution of flow | 2 sampling valves not closed at the same time |  | S* | S* | S* | S* | [28 empty] | 10s | [6 empty] | no | mixing of gas streams causes invalid measurement. Additional operational action: If valve does not close or open in 5 s after command, corresponding command is triggered twice. If the valve does not react after second command trip is initiated. | 25.04.2025 implemented change | F. Reinhart | V1.3: comment changed, Delay changed to 20s in order to allow simultaneously opening of 2 sampling valves (for smoother switchover and continous flow) 22.05.2023: PolGr führt auf H2 Seite im Normalbetrieb nicht zu einer Fremdgaserhöhung V2.0 2023-08-16: Shut down of rectifier/polrect/N2 purge only in S* V2.0: 2023-08-31 (JS, BM): MV circuit braker deleted. | Checked OK 20-04-2026 PD | bar: S* S* to S* S
|  |  | G01NHC01BQ001-QM12 | XB02 |  | Valve does not close |  | bool | zwei volle Durchtaktungen |  |  | Flow O2 in H2 (discont.)
|  |  | G01NHC01BQ001-QM13 | XB02 |  | Valve does not close |  | bool | zwei volle Durchtaktungen |  |  | Flow O2 in H2 (discont.)
|  |  | G01NHC01BQ001-QM14 | XB02 |  | Valve does not close |  | bool | zwei volle Durchtaktungen |  |  | Flow O2 in H2 (discont.)
|  |  | G01NHC01BQ001-QM15 | XB02 |  | Valve does not close |  | bool | zwei volle Durchtaktungen |  |  | Flow O2 in H2 (discont.)
|  |  | G01NHC01BQ001-QM16 | XB02 |  | Valve does not close |  | bool | zwei volle Durchtaktungen |  |  | Flow O2 in H2 (discont.)
|  |  | G01NHC01BQ001-QM17 | XB02 |  | Valve does not close |  | bool | zwei volle Durchtaktungen |  |  | Flow O2 in H2 (discont.)
|  |  | G01NHC01BQ001-QM24 | XB02 |  | Valve does not close |  | bool | zwei volle Durchtaktungen |  |  | Flow O2 in H2 (discont.)
| GA_H2_SWC_ERR | 3.2 | G01NHC01BQ001-QM11 | XB02 | - | 1 | - | BOOL | 640 s |  | 1oo7 | Gasanalytic H2 - Switching error | sampling valve closed for longer than time needed for one measuring cycle |  | S* | S* | S* | S* | [28 empty] | 10s | [6 empty] | no | time needs to be adjusted to fit at least one full measurement cycle | 25.04.2025 implemented change | F. Reinhart | 22.05.2023: PolGr führt auf H2 Seite im Normalbetrieb nicht zu einer Fremdgaserhöhung V2.0 2023-08-16: Shut down of rectifier/polrect/N2 purge only in S* V2.0: 2023-08-31 (JS, BM): MV circuit braker deleted. V3.2, BM, 2024-05-15: Taktung der Magnetventile von 30 s auf 60 s angehoben (Basis: Totzeitbetrachtung BASF), delay von 400 auf 640 s angehoben (FR: "Pro Modulgruppe müssen wir mit der neuen Messzeit dann mit ca. 80s im Worst case rechnen (60s Messzeit + 20s für die Ventilansteuerung (evtl. zweimal hintereinander), Abspeichern des Messwerts, Sicherheitspuffer). Da wir die Validierung auch berücksichtigen müssen, würde ich dann 8 x 80s = 640s rechnen. Vorher war die Rechnung 8 x 50s = 400s.") | Checked OK 20-04-2026 PD | bar: S* S* to S* S
|  |  | G01NHC01BQ001-QM12 | XB02 | - | 1 | - | BOOL
|  |  | G01NHC01BQ001-QM13 | XB02 | - | 1 | - | BOOL
|  |  | G01NHC01BQ001-QM14 | XB02 | - | 1 | - | BOOL
|  |  | G01NHC01BQ001-QM15 | XB02 | - | 1 | - | BOOL
|  |  | G01NHC01BQ001-QM16 | XB02 | - | 1 | - | BOOL
|  |  | G01NHC01BQ001-QM17 | XB02 | - | 1 | - | BOOL
| GA_H2_VAL_ERR | 2.0 | G01NHC01BQ001-QM24 | XB02 | - | 1 | - | BOOL | 1 day |  | 1oo1 | Gasanalytic H2 - Validation error | validation gas valve closed for longer than time needed for one measuring cycle |  | S* | S* | S* | S* | [28 empty] | 10s | [6 empty] | no | time needs to be adjusted in accordence with required validation frequency | 25.04.2025 implemented change | F. Reinhart | 22.05.2023: PolGr führt auf H2 Seite im Normalbetrieb nicht zu einer Fremdgaserhöhung V2.0 2023-08-16: Shut down of rectifier/polrect/N2 purge only in S* V2.0: 2023-08-31 (JS, BM): MV circuit braker deleted. | Checked OK 20-04-2026 PD Checked for 1 Minute instead of 1 Day | bar: S* S* to S* S
Gas Analytic O2 side - G01NHE01BQ001-BQ01 (discont.)
| CCN_GA_O2_HL | 3.2 | G01NHE01BQ001-BQ01 | XQ01 | - | AZHHH 2.0 | 0.1 | % | - | and | 1oo2* | Concentration - Gas analytic O2 - High limit | Concentration of sensor 1 |  | S* | S* | S* | S* | S | S | S | S |  |  |  | S* | S* | NP* | NP* | NP* | NP* | NP* | NP* | NP* | [11 empty] | S | 10s | [6 empty] | no | adjust acc. to requirements of downstream systems (Customer/DeOxo) *One sensor fault (GA_O2_S1_NOT_RDY or GA_O2_S2_NOT_RDY): Bypass of affected Sensor due to faulty sensor and logic is degraded from 1oo2 to 1oo1. After a delay of 72 h the SIF is tripped. In case of two sensor faults (GA_O2_S1_NOT_RDY and GA_O2_S2_NOT_RDY) the SIF is tripped without delay. | 25.04.2025 implemented change | F. Reinhart | V1.3: Warning changed V1.4: Warning not required because already implemented in operational logic (same sensor) 22.05.2023: PolGr von S auf S* geändert, da bereits über N2 Spülung geschützt 25.05.2023: Produktgasventil von NP auf NP* geändert. Info: H2 Seite muss in S gespült werden, da das Refinement die Ursache für FG sein kann. Mit Spülung auf H2 Seite wird kein H2 mehr auf O2 Seite gefördert. V2.0 2023-08-11: failure in module or slow degradation. Purging not required in S. Refinement failure covered by SIS trip of refinement pump-> no purge in S required V2.0: 2023-08-31 (JS, BM): MV circuit braker deleted. V3.1, V2.1 (FR, 01.02.2024): CMD_PRD_VLV_CLS changed from NP* to S* to keep closed after purge V3.2, BM, RW, JS, 2024-07-01: "sensor fault" and "bad signal" deleted since covered by "GA_NOT_RDY"; additionally (1oo3, before 1oo2) "GA_Not_RDY" included. | Checked OK 20-04-2026 PD
|  |  | G01NHE01BQ001-BQ02 | XQ01 | - | AZHHH 2.0 | 0.1 | % | - | and |  |  | Concentration of sensor 2 | bar: S* S to S* NP*
| GA_O2_S1_NOT_RDY | 3.3 | G01NHE01BQ001-QM27 | XB02 | - | 0 | - | Bool | - |  | 1oo6 | Gas analytic O2 - Sensor 1 not ready | 0= cal. valve in calibration pos. | [33 empty] | 10s |  |  | N* |  |  |  | no | - Sensor Drift (KZ31) is Delta between saved Gas Concentration during Validation (KZ10/KZ20) and saved Setpoint [SP] of Validation Gas (KZ71) - the Setpoint of the Validation Gas is also saved and only updated when a new Gas Concentration for Validation Gas is saved (i.e. changing the Setpoint is possible without influencing the last evaluation) - warning/alarm message for calibration request on sensor drift - min flow at L 10.0 l/h * limit values depend on Setpoint [SP] of Validation Gas, e.g. for validation gas of 1.2 Vol% the alarm values should be ASLL -0.12 Vol% (-10% of 1.2 Vol%) and ASHH 0.3 Vol% (25% of 1.2 Vol%) |  | F.Reinhart | V1.3: Warning changed 22.05.2023: PolGr von S auf S* geändert, da bereits über N2 Spülung geschützt 25.05.2023: Spülung wieder eingefügt, damit Refinement nicht abgeschaltet werden muss (Problematisch: Anstieg FG durch Refinmentbetrieb); Produktgasventil von NP auf NP* geändert V2.0 2023-08-16: Shut down of rectifier/polrect/N2 purge only in S* V2.0: 2023-08-31 (JS, BM): MV circuit braker deleted. V3.1, V2.1 (FR, 01.02.2024): CMD_PRD_VLV_CLS changed from NP* to S* to keep closed after purge V3.2, 2024-07-01, BM, RW, JS, FR: GA not ready split up in S1 and S2. Actors (rectifier STO & N2 purge deleted. instead "GA Not Ready"; Sensor drift included from operational part V3.3, 2025-05-13, FR+RW: the limit values are dynamic and depend on the Setpoint of the Validation Gas; Sensor Drift and Setpoint are saved until new measurement of validation gas | Checked OK 20-04-2026 PD
|  |  | G01NHE01BQ001-BF01 | XG02 | - | 0 | - | Bool | 10 s |  |  |  | 0= low flow of sensor 1
|  |  | G01NHE01BQ001-BQ01 | XQ01_BAD | - | 1 | - | Bool | - |  |  |  | 1= bad signal of sensor 1
|  |  | G01NHE01BQ001-BQ01 | XM01 | - | 0 | - | Bool | - |  |  |  | 0= fault of gas sensor 1
|  |  | G01NHE01BQ001-KZ31 | XQ01 | AL -8% SP* | ASLL -10% SP* | - | Delta Vol % | - |  |  |  | sensor drift low of gas sensor 1 (signal from BPCS)
|  |  | G01NHE01BQ001-KZ31 | XQ01 | AH 20% SP* | ASHH 25% SP* | - | Delta Vol % | - |  |  |  | sensor drift high of gas sensor 1 (signal from BPCS)
| GA_O2_S2_NOT_RDY | 3.3 | G01NHE01BQ001-QM23 | XB02 | - | 0 | - | Bool | - |  | 1oo6 | Gas analytic O2 - Sensor 2 not ready | 0= cal. valve in calibration pos. | [37 empty] | N* |  |  | no |  |  | F.Reinhart |  | Checked OK 20-04-2026 PD
|  |  | G01NHE01BQ001-BF02 | XG02 | - | 0 | - | Bool | 10 s |  |  |  | 0= low flow of sensor 2
|  |  | G01NHE01BQ001-BQ02 | XQ01_BAD | - | 1 | - | Bool | - |  |  |  | 1= bad signal of sensor 2
|  |  | G01NHE01BQ001-BQ02 | XM01 | - | 0 | - | Bool | - |  |  |  | 0= fault of gas sensor 2
|  |  | G01NHE01BQ001-KZ32 | XQ01 | AL -8% SP* | ASLL -10% SP* | - | Delta Vol % | - |  |  |  | sensor drift low of gas sensor 2 (signal from BPCS)
|  |  | G01NHE01BQ001-KZ32 | XQ01 | AH 20% SP* | ASHH 25% SP* | - | Delta Vol % | - |  |  |  | sensor drift high of gas sensor 2 (signal from BPCS) |  | S | S | S | S | S | S | S | S | [24 empty] | 10s
| GA_O2_DIL_FLW | 2.0 | G01NHE01BQ001-QM11 | XB02 | - | 0 | - | BOOL | 20 s |  | 2oo7 | Gasanalytic O2 - Dilution of flow | 2 sampling valves not closed at the same time |  | S* | S* | S* | S* | [28 empty] | 10s | [6 empty] | no | mixing of gas streams causes invalid measurement. Additional operational action: If valve does not close or open in 5 s after command, corresponding command is triggered twice. If the valve does not react after second command trip is initiated. | 25.04.2025 implemented change | F. Reinhart | V1.3: comment changed, Delay changed 22.05.2023: PolGr von S auf S* geändert, da bereits über N2 Spülung geschützt V2.0 2023-08-16: Shut down of rectifier/polrect/N2 purge only in S* V2.0: 2023-08-31 (JS, BM): MV circuit braker deleted. | Checked OK 20-04-2026 PD | bar: S* S* to S* S
|  |  | G01NHE01BQ001-QM12 | XB02 |  | Valve does not close |  | bool | zwei volle Durchtaktungen |  |  | Flow O2 in H2 (discont.)
|  |  | G01NHE01BQ001-QM13 | XB02 |  | Valve does not close |  | bool | zwei volle Durchtaktungen |  |  | Flow O2 in H2 (discont.)
|  |  | G01NHE01BQ001-QM14 | XB02 |  | Valve does not close |  | bool | zwei volle Durchtaktungen |  |  | Flow O2 in H2 (discont.)
|  |  | G01NHE01BQ001-QM15 | XB02 |  | Valve does not close |  | bool | zwei volle Durchtaktungen |  |  | Flow O2 in H2 (discont.)
|  |  | G01NHE01BQ001-QM16 | XB02 |  | Valve does not close |  | bool | zwei volle Durchtaktungen |  |  | Flow O2 in H2 (discont.)
|  |  | G01NHE01BQ001-QM24 | XB02 |  | Valve does not close |  | bool | zwei volle Durchtaktungen |  |  | Flow O2 in H2 (discont.)
| GA_O2_SWC_ERR | 3.2 | G01NHE01BQ001-QM11 | XB02 | - | 1 | - | BOOL | 640 s |  | 1oo6 | Gasanalytic O2 - Switching error | sampling valve closed for longer than time needed for one measuring cycle |  | S* | S* | S* | S* | [28 empty] | 10s | [6 empty] | no | time needs to be adjusted to fit at least one full measurement cycle Monitor if sequenz is working correctly and not that one SV is open for longer time and no sample switching occurs. | 25.04.2025 implemented change | F. Reinhart | 22.05.2023: PolGr von S auf S* geändert, da bereits über N2 Spülung geschützt V2.0 2023-08-16: Shut down of rectifier/polrect/N2 purge only in S* V2.0: 2023-08-31 (JS, BM): MV circuit braker deleted. V.3.0: 2024-1-5: (FR; RW): Bug fix "Delay Time for each individual signal" => analog H2 Measurement V3.2, BM, 2024-05-15: Taktung der Magnetventile von 30 s auf 60 s angehoben (Basis: Totzeitbetrachtung BASF), delay von 400 auf 640 s angehoben (FR: "Pro Modulgruppe müssen wir mit der neuen Messzeit dann mit ca. 80s im Worst case rechnen (60s Messzeit + 20s für die Ventilansteuerung (evtl. zweimal hintereinander), Abspeichern des Messwerts, Sicherheitspuffer). Da wir die Validierung auch berücksichtigen müssen, würde ich dann 8 x 80s = 640s rechnen. Vorher war die Rechnung 8 x 50s = 400s.") | Checked OK 20-04-2026 PD | bar: S* S* to S* S
|  |  | G01NHE01BQ001-QM12 | XB02 | - | 1 | - | BOOL
|  |  | G01NHE01BQ001-QM13 | XB02 | - | 1 | - | BOOL
|  |  | G01NHE01BQ001-QM14 | XB02 | - | 1 | - | BOOL
|  |  | G01NHE01BQ001-QM15 | XB02 | - | 1 | - | BOOL
|  |  | G01NHE01BQ001-QM16 | XB02 | - | 1 | - | BOOL
| GA_O2_VAL_ERR | 2.0 | G01NHE01BQ001-QM24 | XB02 | - | 1 | - | BOOL | 1 day |  | 1oo1 | Gasanalytic O2 - Validation error | validation gas valve closed for longer than time needed for one measuring cycle |  | S* | S* | S* | S* | [28 empty] | 10s | [6 empty] | no | time needs to be adjusted in accordience with required validation frequency | 25.04.2025 implemented change | F. Reinhart | V2.0 2023-08-16: Shut down of rectifier/polrect/N2 purge only in S* V2.0: 2023-08-31 (JS, BM): MV circuit braker deleted. | Checked OK 20-04-2026 PD | bar: S* S* to S* S
Rectifier Current Customer's scope
| D_CUR_REC1&2_HL | 3.1 | G01NHA01BZ011-KZ02 | XQ01 | - | AZH ¦500.0¦ |  | A | 2s |  | 2oo2 | Delta between Rect1 and Rect2 too high (delta > 500 A) & rectifier current too low or too high - DCM control failure | too high delta between Rectifier currents |  | S* | S* | S* | S* | S | S | [5 empty] | S* | S* | NP* | NP* | NP* | NP* | NP* | NP* | NP* | [19 empty] | 5 h | Internal control failure of DCM leads to too low or too high current of one rectifier row. N2 purge shall start after array shutdown. Max.allowable trip value for delta is 500 A. If current measurement signal is "bad quality" or lost, protection loop shall be triggered. | 25.04.2025 implemented change | F. Reinhart | V1.4 added due to QIS item (DCM control failure) V2.0: 28.08.2023 (BM) Falls das Stromsignal verloren geht soll der Schutzkreis auslösen. Es soll kein Ersatzwert gebildet werden. V2.0: 2023-08-31 (JS, BM): N2 purge not part of SIL loop, since local zones are small and not considered dangerous. V3.0, BM, 25.10.2023: TAG numbers of SIS Measurment changed BM, 8.11.2023: Name of loop identifier changed V3.1, V2.1 (FR, 01.02.2024): CMD_PRD_VLV_CLS changed from NP* to S* to keep closed after purge | Checked OK 20-04-2026 PD Simulation is not correctly working as Current
|  |  | G01NHA01BZ011-BC01 | XQ01 | - | L 2500 |  | A | - | or
|  |  | G01NHA01BZ012-BC01 | XQ01
|  |  | G01NHA01BZ011-BC01 | XQ01 | - | H 8000 |  | A | -
|  |  | G01NHA01BZ012-BC01 | XQ01
| D_CUR_REC3&4_HL | 3.1 | G01NHA01BZ013-KZ02 | XQ01 | - | AZH ¦500.0¦ |  | A | 2s |  | 2oo2 | Delta between Rect3 and Rect4 too high (delta > 500 A) & rectifier current too low or too high - DCM control failure | too high delta between Rectifier currents |  | S* | S* | S* | S* |  |  | S | S |  |  |  | S* | S* | NP* | NP* | NP* | NP* | NP* | NP* | NP* | [19 empty] | 5 h |  | 25.04.2025 implemented change | F. Reinhart |  | Checked OK 20-04-2026 PD Simulation is not correctly working as Current
|  |  | G01NHA01BZ013-BC01 | XQ01 | - | L 2500 |  | A | - | or
|  |  | G01NHA01BZ014-BC01 | XQ01
|  |  | G01NHA01BZ013-BC01 | XQ01 | - | H 8000 |  | A | -
|  |  | G01NHA01BZ014-BC01 | XQ01
N2 Supply
| PRS_N2_SUP1_LL | 2.0 | G01NHX01QN001-BP01 | XQ01 | AL 1.2 | AZLLL 0.5 | 0.2 | bar(g) | - |  | 1oo1 | N2 supply pressure low | H2 side | [10 empty] | S* | S | [21 empty] | 10s | [6 empty] | no | N2 Supply not available, cross-flow O2/H2 sides over NHX system must be prevented. SIS purge (opening of blow off valves, shut off valve H2 side and closing of product gas valve) shall not be interlocked.-> after 15 min SIS purge is failed and blow off valves will close again. | 25.04.2025 no change | F. Reinhart | V1.4 separated 1oo2 logic into 2x 1oo1 logic, because easier to handle with typicals and COMOS V2.0 2023-08-16: Shut down of rectifier/polrect in S deleted. Interlock is considered in operational part. | Checked OK 20-04-2026 PD
| PRS_N2_SUP2_LL | 2.0 | G01NHX01QN002-BP01 | XQ01 | AL 1.2 | AZLLL 0.5 | 0.2 | bar(g) | - |  | 1oo1 | N2 supply pressure low | O2 side | [10 empty] | S* | S | [21 empty] | 10s | [6 empty] | no |  | 25.04.2025 no change | F. Reinhart |  | Checked N.OK 20-04-2026 PD Change Safety Matrix tag
Emergency Stop (Thyripol)
| EM_STOP_RECT | 3.3 | G01NHA01KF001-SF01 | XW01/02 | - | 0 | - | BOOL | - |  | 1oo1 | Emergency Stop - Rectifier Cabinet | ESD Rectifier Control Cabinet |  | S* | S* | S* | S* | [16 empty] | S* | [11 empty] | 1s | [6 empty] | no | -Manual pushbutton on rectifier I&C cabinet -project specific definition of door switches and ESD buttonsthat shall be considered - control does not initiate opening of DC disconnectors and discharging by discharge resistors -> rest voltage stays active | 25.04.2025 implemented change | F. Reinhart | N2 purge deleted.Cause identifier changed from EM_STOP to EM_STOP_RECT V3.2, 2024-03-11 (BM) comment added: "- control does not initiate opening of DC disconnectors and discharging by discharge resistors -> rest voltage stays active" V3.3 seperated into an individual cause | Checked N.OK 20-04-2026 PD Rename Safety Matrix tag to NHA01TB001-SF01 | bar: S* S* to S* S
| DOOR_CTC_RECT | 3.3 | G01NHA01QQ001-BG01 | XW01/02 | - | 0 | - | BOOL | - |  | 1oo1 | Door Contact - Recifier Room | Door contact rectifier room (supplied by customer) OPTIONAL |  | S* | S* | S* | S* | [16 empty] | S* | [18 empty] | no | Project specific decision if needed. Normally organizational measures (lock at door) are sufficient for rectifier room access. See building requirements and HAZOP. If door contact is used, the rectifier shut down shall be followed by automatic start of maintenance step sequence which activates discharge resistors.- Rectifer door contact to be deactivated for commissioning purpose only To be disussed with customer & Nichicon | 25.04.2025 implemented change | F. Reinhart | V2.0, 2023-08-30: Comment for door switches added. V3.1, 2024-01-17 (RW, FR, BM): door contacts and RDS for signals and switsches updated (fence and door contact new) V3.3 seperated into an individual cause V3.3, BM, FR, JS: Door contact only optional. If automatic shut dwown is considered automatic discharge shall be considered as well. | Checked N.OK 21-04-2026 PD Rename Safety Matrix tag to NHA01KF003-SF01 Voting Logic is not implemented in Program. | bar: S* S* to S* S
| DOOR_CTC_ARRAY | 3.3 | G01NHY01QQ001-BG01 | XW01/02 | - | 0 | - | BOOL | - |  | 1oo1 | Door Contact - Array Fence | Door contact - Array Fence (optional, supplied by customer) OPTIONAL |  | S* | S* | S* | S* | [16 empty] | S* | [18 empty] | no | Project specific decision if needed. Normally organizational measures (lock at gate) are sufficient for array access. See building requirements and HAZOP. If door contact is used, the rectifier shut down shall be followed by automatic start of maintenance step sequence which activates discharge resistors. The "MV Circuit Breaker" should be tripped only, when the AC side of the rectifiers can be accessed from the Array fence area. In projects with a separate rectifier room, the trip of the "MV Circuit Breaker" is not required. To be disussed with customer & Nichicon | 25.04.2025 implemented change | F. Reinhart | V3.3, 2025-04-01 (FR, FP): changed Door contact Array Fence "G01NHY01KF001-BG01" to "G01NHY01QQ01-BG01", seperated into an individual cause V3.3, BM, FR, JS: Door contact only optional. If automatic shut dwown is considered automatic discharge shall be considered as well. | Checked N.OK 20-04-2026 PD Rename Safety Matrix tag to NHY01KF003-BG01 Voting Logic is not implemented in Program. | bar: S* S* to S* S
| EM_STOP_ARRAY | 3.3 | G01NHY01KF001-SF01 | XW01/02 | - | 0 | - | BOOL | - |  | 1oo1 | Emergency Stop - Array Cabinet | Array I&C Cabinet |  | S* | S* | S* | S* | [7 empty] | S* | S* | NP* | NP* | NP* | NP* | NP* | NP* | NP* | [12 empty] | 1s | [6 empty] | no | -Manual pushbutton on array I&C cabinet | 25.04.2025 implemented change | F. Reinhart | V2.0: 2023-08-31 (JS, RW, BM) added as new loop. V3.1, 2024-01-17 (RW, FR, BM): Rectifier ESD button changed to ESD of Array I&C. Plant ESD deleted since already covered by BoP part. V3.1, V2.1 (FR, 01.02.2024): CMD_PRD_VLV_CLS changed from NP* to S* to keep closed after purge V3.3 (FR, 01.04.2024): "1ooX" changed to "1oo1", seperated into an individual cause | Checked N.OK 21-04-2026 PD Rename Safety Matrix tag to NHA01KF003-SF01 Voting Logic is not implemented in Program.
Transformer (Thyripol) Customer's To be deleted
| TRF_BHZ_PROT | 1.3 | G01NHA01TA001-BU01 | XM02 | - | 0 | - | BOOL | - |  | 1oo1 | Buchholz Protection | also hardwired connection |  | S* | S* | S* | S* | [16 empty] | S* | [11 empty] | 10s | [6 empty] | no |  | 25.04.2025 implemented change | P. Kumar
| TMP_WND_TRF_HL | 1.3 | G01NHA01TA001-BT02 | XM02 | - | 0 | - | BOOL | - |  | 1oo1 | Winding Temperature Transformer High |  |  | S* | S* | S* | S* | [16 empty] | S* | [11 empty] | 10s | [6 empty] | no |  | 25.04.2025 implemented change | P. Kumar
| TMP_OIL_TRF_HL | 1.3 | G01NHA01TA001-BT01 | XM02 | - | 0 | - | BOOL | - |  | 1oo1 | Oil temp. Transformer High | also hardwired to MV CB |  | S* | S* | S* | S* | [16 empty] | S* | [11 empty] | 10s | [6 empty] | no |  | 25.04.2025 implemented change | P. Kumar
| PRS_OIL_TRF_HL | 1.3 | G01NHA01TA001-BP01 | XM02 | - | 0 | - | BOOL | - |  | 1oo1 | Transformer Oil pressure High | also hardwired connection |  | S* | S* | S* | S* | [16 empty] | S* | [11 empty] | 10s | [6 empty] | no |  | 25.04.2025 implemented change | P. Kumar
| PRS_OIL_TCH_HL | 3.1 | G01NHA01TA001-BP02 | XM02 | - | 0 | - | BOOL | - |  | 1oo1 | Tap Changer Oil pressure High | also hardwired connection |  | S* | S* | S* | S* | [16 empty] | S* | [11 empty] | 10s | [6 empty] | no |  | 25.04.2025 implemented change | P. Kumar | V3.1 (BM): added as new cause & effect in V2.1
| TMP_OIL_TCH_HL | 1.3 | G01NHA01TA001-BU02 | XM01 | - | 0 | - | BOOL | - |  | 1oo1 | Tap changer Protective Relay | also hardwired connection |  | S* | S* | S* | S* | [16 empty] | S* | [11 empty] | 10s | [6 empty] | no | no pre-alarm available | 25.04.2025 implemented change | P. Kumar
| CUR_1&2_TRF_HL | 1.3 | G01NHA01TA001-FC01 | XG01 | - | 0 | - | BOOL | - |  | 1oo1 | Overcurrent protection 1 & 2 | also hardwired connection |  | S* | S* | S* | S* | [16 empty] | S* | [11 empty] | 10s | [6 empty] | no | pre-alarm seperate (pick-up) | 25.04.2025 implemented change | P. Kumar
| CUR_3&4_TRF_HL | 1.3 | G01NHA01TA001-FC02 | XG01 | - | 0 | - | BOOL | - |  | 1oo1 | Overcurrent protection 3 & 4 | also hardwired connection |  | S* | S* | S* | S* | [16 empty] | S* | [11 empty] | 10s | [6 empty] | no | pre-alarm seperate (pick-up) | 25.04.2025 implemented change | P. Kumar
| TCH_SWC_ERR | 1.4 | G01NHA01TA001-QA02 | XM01 | - | 0 | - | BOOL | - |  | 1oo1 | Tap changer incomplete switching |  |  | S* | S* | S* | S* | [16 empty] | S* | [11 empty] | 10s | [6 empty] | no | no pre-alarm available | 25.04.2025 implemented change | P. Kumar
Rectifier System (Scope to be clarified)
| DC-_REC1_HWL_PLG | 3.3 | G01NHA01QZ001-QB02 | XV01 | - | 0 | - | BOOL | - |  | 1oo1 | Rectifier 1 DC- disconnector Handwheel plugged | DC- handwheel plugged |  | N* |  |  |  | N* | [20 empty] | N* | [6 empty] | - | [6 empty] | no | Operation of disconnectors and rectifiers blocked when hand wheel of DC disconnetors is plugged. | 11.03.2025 No change | P.Kumar | V3.0, BM, 8.11.2023: new modular rectifier design V3.3, BM+FR, 16.10.2024: N* added to block disconnector operation deleted "During operation of rectifiers the trip is not active" | Checked .OK 21-04-2026 PD
| DC-_REC2_HWL_PLG | 3.3 | G01NHA01QZ002-QB02 | XV01 | - | 0 | - | BOOL | - |  | 1oo1 | Rectifier 2 DC- disconnector Handwheel plugged |  |  |  | N* |  |  |  | N* | [20 empty] | N* | [5 empty] | - | [6 empty] | no |  | 11.03.2025 No change | P.Kumar |  | Checked .OK 21-04-2026 PD
| DC-_REC3_HWL_PLG | 3.3 | G01NHA01QZ003-QB02 | XV01 | - | 0 | - | BOOL | - |  | 1oo1 | Rectifier 3 DC- disconnector Handwheel plugged |  |  |  |  | N* |  |  |  | N* | [20 empty] | N* |  |  |  |  | - | [6 empty] | no |  | 11.03.2025 No change | P.Kumar |  | Checked .OK 21-04-2026 PD
| DC-_REC4_HWL_PLG | 3.3 | G01NHA01QZ004-QB02 | XV01 | - | 0 | - | BOOL | - |  | 1oo1 | Rectifier 4 DC- disconnector Handwheel plugged | [5 empty] | N* |  |  |  | N* | [20 empty] | N* |  |  |  | - | [6 empty] | no |  | 11.03.2025 No change | P.Kumar |  | Checked .OK 21-04-2026 PD
| DC+_REC1_HWL_PLG | 3.3 | G01NHA01QZ001-QB01 | XV01 | - | 0 | - | BOOL | - |  | 1oo1 | Rectifier 1 DC+ disconnector Handwheel plugged | DC+ handwheel plugged |  | N* |  |  |  | N* | [16 empty] | N* | [10 empty] | - | [6 empty] | no |  | 11.03.2025 No change | P.Kumar |  | Checked .OK 21-04-2026 PD
| DC+_REC2_HWL_PLG | 3.3 | G01NHA01QZ002-QB01 | XV01 | - | 0 | - | BOOL | - |  | 1oo1 | Rectifier 2 DC+ disconnector Handwheel plugged |  |  |  | N* |  |  |  | N* | [16 empty] | N* | [9 empty] | - | [6 empty] | no |  | 11.03.2025 No change | P.Kumar |  | Checked .OK 21-04-2026 PD
| DC+_REC3_HWL_PLG | 3.3 | G01NHA01QZ003-QB01 | XV01 | - | 0 | - | BOOL | - |  | 1oo1 | Rectifier 3 DC+ disconnector Handwheel plugged |  |  |  |  | N* |  |  |  | N* | [16 empty] | N* | [8 empty] | - | [6 empty] | no |  | 11.03.2025 No change | P.Kumar |  | Checked .OK 21-04-2026 PD
| DC+_REC4_HWL_PLG | 3.3 | G01NHA01QZ004-QB01 | XV01 | - | 0 | - | BOOL | - |  | 1oo1 | Rectifier 4 DC+ disconnector Handwheel plugged | [5 empty] | N* |  |  |  | N* | [16 empty] | N* | [7 empty] | - | [6 empty] | no |  | 11.03.2025 No change | P.Kumar |  | Checked .OK 21-04-2026 PD
| CMD_REC1_OFF_FLT | 3.3 | G01NHA01TB001-KF01 | XB02 | - | 1 | - | BOOL | - | or | 2oo2 | Rectifier 1 Protection Command (E-Stop) Fault | 1= Prot. Feedback Off not active | [5 empty] | S* | [34 empty] | no | On fault of Protection Command Off (E-Stop) of rectifier, i.e. Feedback Off does not come within 3s after command, activate Safe Current Off (SCO). | 07.04.2025 implemented change | F.Poeppel | V3.3, FR+BM, 15.10.2024: added cause V3.3, BM+FR+AD, 02.04.2025: Feedback changed from 0=active to 1=active; "STO" changed to "Prot. Cmd. (E-Stop)", added evaluation of SIL Current Measurement to determine whether Command Off was successful, because Feedback of Prot. Cmd is not reliable enough | Checked OK 21-04-2026 PD
|  |  | G01NHA01BZ011-BC01 | XQ01 | - | H 100 | - | A | - |  |  |  | SIL Current Meas. > 100A
|  |  | G01NHA01TB001-KF01 | YB32 | - | 0 | - | BOOL | 3 s |  |  |  | 0= Prot. Cmd. (E-Stop) active
| CMD_REC2_OFF_FLT | 3.3 | G01NHA01TB002-KF01 | XB02 | - | 1 | - | BOOL | - | or | 2oo2 | Rectifier 2 Protection Command (E-Stop) Fault | 1= Prot. Feedback Off not active | [6 empty] | S* | [33 empty] | no |  | 07.04.2025 implemented change | F.Poeppel |  | Checked OK 21-04-2026 PD
|  |  | G01NHA01BZ012-BC01 | XQ01 | - | H 100 | - | A | - |  |  |  | SIL Current Meas. > 100A
|  |  | G01NHA01TB002-KF01 | YB32 | - | 0 | - | BOOL | 3 s |  |  |  | 0= Prot. Cmd. (E-Stop) active
| CMD_REC3_OFF_FLT | 3.3 | G01NHA01TB003-KF01 | XB02 | - | 1 | - | BOOL | - | or | 2oo2 | Rectifier 3 Protection Command (E-Stop) Fault | 1= Prot. Feedback Off not active | [7 empty] | S* | [32 empty] | no |  | 07.04.2025 implemented change | F.Poeppel |  | Checked OK 21-04-2026 PD
|  |  | G01NHA01BZ013-BC01 | XQ01 | - | H 100 | - | A | - |  |  |  | SIL Current Meas. > 100A
|  |  | G01NHA01TB003-KF01 | YB32 | - | 0 | - | BOOL | 3 s |  |  |  | 0= Prot. Cmd. (E-Stop) active
| CMD_REC4_OFF_FLT | 3.3 | G01NHA01TB004-KF01 | XB02 | - | 1 | - | BOOL | - | or | 2oo2 | Rectifier 4 Protection Command (E-Stop) Fault | 1= Prot. Feedback Off not active | [8 empty] | S* | [31 empty] | no |  | 07.04.2025 implemented change | F.Poeppel |  | Checked OK 21-04-2026 PD
|  |  | G01NHA01BZ014-BC01 | XQ01 | - | H 100 | - | A | - |  |  |  | SIL Current Meas. > 100A
|  |  | G01NHA01TB004-KF01 | YB32 | - | 0 | - | BOOL | 3 s |  |  |  | 0= Prot. Cmd. (E-Stop) active
| REC1_NOT_OFF | 3.3 | G01NHA01BZ011-BC01 | XQ01 | - | H 100 | - | A | - |  | 1oo1 | Rectifier 1 not off | SIL Current Meas. > 100A | [22 empty] | N* |  |  |  | N* | [13 empty] | no | Opening of DC disconnectors blocked while rectifiers in operation (>100 A). Only status message shall be triggered on this cause, as this is not a fault condition. | 07.04.2025 implemented change | F.Poeppel | V3.0, BM, 8.11.2023: new modular rectifier design V3.3, FR, 01.10.2024: STO and SCO not active (2oo2) instead of STO/E-Stop (1oo2), otherwise operational opening of DC disconnectors would not work V3.3, BM, 02.04.2025: Fedback changed from 0=active to 1=active; "STO" changed to "Prot. Cmd. (E-Stop)", added evaluation of SIL Current Measurement to determine whether Rectifier is Off, because Feedback of Prot. Cmd is not reliable enough V3.3, FR+AD, 04.04.2025: simplified to 1oo1 after discussion with Arne: it should be enough to evaluate the SIL Current Measurement, Disconnectors are only opened operationally after the rectifier pulses were disabled and the E-Stop was activated. If SIL Current Measurement does not work correctly, the rectifiers are blocked via Delta Current SIF already | Checked OK 21-04-2026 PD
| REC2_NOT_OFF | 3.3 | G01NHA01BZ012-BC01 | XQ01 | - | H 100 | - | A | - |  | 1oo1 | Rectifier 2 not off | SIL Current Meas. > 100A | [23 empty] | N* |  |  |  | N* | [12 empty] | no |  | 07.04.2025 implemented change | F.Poeppel |  | Checked OK 21-04-2026 PD
| REC3_NOT_OFF | 3.3 | G01NHA01BZ013-BC01 | XQ01 | - | H 100 | - | A | - |  | 1oo1 | Rectifier 3 not off | SIL Current Meas. > 100A | [24 empty] | N* |  |  |  | N* | [11 empty] | no |  | 07.04.2025 implemented change | F.Poeppel |  | Checked OK 21-04-2026 PD
| REC4_NOT_OFF | 3.3 | G01NHA01BZ014-BC01 | XQ01 | - | H 100 | - | A | - |  | 1oo1 | Rectifier 4 not off | SIL Current Meas. > 100A | [25 empty] | N* |  |  |  | N* | [10 empty] | no |  | 07.04.2025 implemented change | F.Poeppel |  | Checked OK 21-04-2026 PD
Note:
1 | There is no specific constant pressure piston buffer tank in H2 Sakura project downstream of product control valve. Hence customer's contant volume tank to be reffered as buffer tank/volume
2 | The cause-and-effect relationships outlined herein are provided solely on the basis of Siemens Energy’s limited experience with complete plant configurations. They are intended for preliminary guidance only and shall not be construed as comprehensive, exhaustive, or finalized from Siemens Energy’s side.
The Customer shall bear full responsibility for conducting detailed investigations, including but not limited to project-specific HAZOP and HAZID studies, to identify any critical causes at the complete plant level that may trigger array safety-related effects.
Any additional causes or effects identified by the Customer may be proposed for inclusion. Incorporation into the safety matrix and associated logic shall be subject to mutual agreement between Siemens Energy and the Customer.
Rectifier Current (IGBT) - OPTIONAL
| D_CUR_REC1&2_HL | 3.3 | G01NHA01BZ011-KZ02 | XQ01 | - | AZH ¦500.0¦ |  | A | 2s |  | 2oo2 | Delta between Rect Row 1 and Rect Row 2 too high (delta > 500 A) & rectifier current too low or too high - DCM control failure | too high delta between Rectifier currents |  | S* | S* |  |  | S | S | [6 empty] | S* | NP* | NP* | NP* | NP* | NP* | NP* | NP* | [20 empty] | Internal control failure of DCM leads to too low or too high current of one rectifier row. N2 purge shall start after array shutdown. Max.allowable trip value for delta is 500 A. If current measurement signal is "bad quality" or lost, protection loop shall be triggered. |  |  | V1.4 added due to QIS item (DCM control failure) V2.0: 28.08.2023 (BM) Falls das Stromsignal verloren geht soll der Schutzkreis auslösen. Es soll kein Ersatzwert gebildet werden. V2.0: 2023-08-31 (JS, BM): N2 purge not part of SIL loop, since local zones are small and not considered dangerous. V3.0, BM, 25.10.2023: TAG numbers of SIS Measurment changed BM, 8.11.2023: Name of loop identifier changed V3.1, V2.1 (FR, 01.02.2024): CMD_PRD_VLV_CLS changed from NP* to S* to keep closed after purge
|  |  | G01NHA01BZ011-BC01 | XQ01 | - | L 2500 |  | A | - | or
|  |  | G01NHA01BZ012-BC01 | XQ01
|  |  | G01NHA01BZ011-BC01 | XQ01 | - | H 8000 |  | A | -
|  |  | G01NHA01BZ012-BC01 | XQ01
Emergency Stop (IGBT) - OPTIONAL
| EM_STOP_RECT | 3.3 | G01NHA01TB001-SF01 | XW01/02 | - | 0 | - | BOOL | - |  | 1ooX | emergency stop rectifier / door contact (rect. room & array fence) | LV Control Panel (IGBT) Row 1 |  | S* | S* |  |  | S | S | [14 empty] | S* | [11 empty] | 1s | [5 empty] | S* |  | -Manual pushbutton on rectifier LV Control cabinet - Rectifer housing door contact to be deactivated for commissioning purpose only - Rectifier housing door contact is implemented in IGBT converter (Ingeteam's scope) - control does not initiate opening of DC disconnectors and discharging by discharge resistors -> rest voltage stays active |  |  | V2.0, 2023-08-30: Comment for door switches added. N2 purge deleted.Cause identifier changed from EM_STOP to EM_STOP_RECT V3.1, 2024-01-17 (RW, FR, BM): door contacts and RDS for signals and switsches updated (fence and door contact new) V3.2, 2024-03-11 (BM) comment added: "- control does not initiate opening of DC disconnectors and discharging by discharge resistors -> rest voltage stays active"
|  |  | G01NHA01TB002-SF01 | XW01/02 | [8 empty] | LV Control Panel (IGBT) Row2
|  |  | G01NHA01QQ001-BG01 | XW01/02 | [8 empty] | Door contact rectifier housing
|  |  | G01NHY01KF001-BG01 Array fence contact | XW01/02 | [8 empty] | Fence door contact (optional, supplied by customer)
Transformer (IGBT) - OPTIONAL
| TRF_BHZ_PROT_ROW1 | 3.3 | G01NHA01TA001-BU01 | XM02 | - | 0 | - | BOOL | - |  | 1oo1 | Buchholz Protection | also hardwired to MV CB | [5 empty] | S* | S* | [14 empty] | S* | [11 empty] | 10s
| TMP_WND_TRF_HL | 3.3 | G01NHA01TA001-BT02 | XM02 | - | 0 | - | BOOL | - |  | 1oo1 | Winding Temperature Transformer High | also hardwired to MV CB | [5 empty] | S* | S* | [14 empty] | S* | [11 empty] | 10s | [7 empty] | project specific
| TMP_OIL_TRF_HL_ROW1 | 3.3 | G01NHA01TA001-BT01 | XM02 | - | 0 | - | BOOL | - |  | 1oo1 | Oil temp. Transformer High | also hardwired to MV CB | [5 empty] | S* | S* | [14 empty] | S* | [11 empty] | 10s
| PRS_OIL_TRF_HL_ROW1 | 3.3 | G01NHA01TA001-BP01 | XM02 | - | 0 | - | BOOL | - |  | 1oo1 | Transformer Oil pressure High | also hardwired to MV CB | [5 empty] | S* | S* | [14 empty] | S* | [11 empty] | 10s
| PRS_OIL_TCH_HL | 3.3 | G01NHA01TA001-BP02 | XM02 | - | 0 | - | BOOL | - |  | 1oo1 | Tap Changer Oil pressure High | also hardwired to MV CB | [5 empty] | S* | S* | [14 empty] | S* | [11 empty] | 10s
| TMP_OIL_TCH_HL_ROW1 | 3.3 | G01NHA01TA001-BU02 | XM01 | - | 0 | - | BOOL | - |  | 1oo1 | Tap changer Protective Relay | also hardwired to MV CB | [5 empty] | S* | S* | [14 empty] | S* | [11 empty] | 10s
| CUR_TRF1_HL | 3.3 | T01BBA01QA00x-BC01 | XM01 | - | 0 | - | BOOL | - |  | 1oo1 | Overcurrent protection Row 1 | integral function of MV CB (not processes in array control) | [21 empty] | S* | [11 empty] | 10s | [7 empty] | Trip and shut down of MV CB directly implemented in MV Switchgear by others. x= number of Array (starting number tbd) AC CB will not be tripped since covered by MV CB feedback (not closed) | bar: S* S*; S* NP* to S* NP*
| CUR_TRF1_HL | 3.3 | T01BBA01QA00x-QA01 | XB01 | - | 0 | - | BOOL | - |  | 1oo2 | MV CB not closed | [6 empty] | S* | S* | [34 empty] | in work
| FB_Maintenance | 3.3 | G01NHY01KF101-KZ74 | XB01 | - | 0 | - | BOOL | - |  |  | Array not in maintenance
| TCH_SWC_ERR_ROW1 | 3.3 | G01NHA01TA001-QA02 | XM01 | - | 0 | - | BOOL | - |  | 1oo1 | Tap changer incomplete switching | [6 empty] | S* | S* | [14 empty] | S* | [11 empty] | 10s
| TRF_BHZ_PROT_ROW2 | 3.3 | G01NHA01TA002-BU01 | XM02 | - | 0 | - | BOOL | - |  | 1oo1 | Buchholz Protection | also hardwired to MV CB | [5 empty] | S* | S* | [26 empty] | 10s | [5 empty] | S*
| TMP_WND_TRF_HL | 3.3 | G01NHA01TA002-BT02 | XM02 | - | 0 | - | BOOL | - |  | 1oo1 | Winding Temperature Transformer High | also hardwired to MV CB | [5 empty] | S* | S* | [26 empty] | 10s | [5 empty] | S* |  | Project specific
| TMP_OIL_TRF_HL_ROW2 | 3.3 | G01NHA01TA002-BT01 | XM02 | - | 0 | - | BOOL | - |  | 1oo1 | Oil temp. Transformer High | also hardwired to MV CB | [5 empty] | S* | S* | [26 empty] | 10s | [5 empty] | S*
| PRS_OIL_TRF_HL_ROW2 | 3.3 | G01NHA01TA002-BP01 | XM02 | - | 0 | - | BOOL | - |  | 1oo1 | Transformer Oil pressure High | also hardwired to MV CB | [5 empty] | S* | S* | [26 empty] | 10s | [5 empty] | S*
| PRS_OIL_TCH_HL | 3.3 | G01NHA01TA002-BP02 | XM02 | - | 0 | - | BOOL | - |  | 1oo1 | Tap Changer Oil pressure High | also hardwired to MV CB | [5 empty] | S* | S* | [26 empty] | 10s | [5 empty] | S*
| TMP_OIL_TCH_HL_ROW2 | 3.3 | G01NHA01TA002-BU02 | XM01 | - | 0 | - | BOOL | - |  | 1oo1 | Tap changer Protective Relay | also hardwired to MV CB | [5 empty] | S* | S* | [26 empty] | 10s | [5 empty] | S*
| CUR_TRF2_HL | 3.3 | T01BBA01QA00x-BC02 | XM01 | - | 0 | - | BOOL | - |  | 1oo1 | Overcurrent protection Row 2 | integral function of MV CB (not processes in array control) | [33 empty] | 10s | [5 empty] | S* |  | Trip and shut down of MV CB directly implemented in MV Switchgear by others. x= number of Array (starting number tbd) AC CB will not be tripped since covered by MV CB feedback (not closed) | bar: S* S*; S* NP* to S* NP*
| CUR_TRF1_HL | 3.3 | T01BBA01QA00x-QA02 | XB01 | - | 0 | - | BOOL | - |  | 1oo2 | MV CB not closed | [6 empty] | S* | S*
| FB_Maintenance | 3.3 | G01NHY01KF101-KZ74 | XB01 | - | 0 | - | BOOL | - |  |  | Array not in maintenance
| TCH_SWC_ERR_ROW2 | 3.3 | G01NHA01TA002-QA02 | XM01 | - | 0 | - | BOOL | - |  | 1oo1 | Tap changer incomplete switching | [6 empty] | S* | S* | [26 empty] | 10s | [5 empty] | S*
Rectifier System (IGBT) - OPTIONAL
| AC_RW1_NC | 3.3 | G01NHA01QZ001-QB10 | XB01 | - | 0 | - | BOOL | - |  | 1oo4 | AC CB Rectifier Row 1 Not ON (not closed) | AC CBs not closed |  | N* | N* | [38 empty] | Start of rectifiers blocked when AC disconnectors are not closed. During operation of rectifiers the trip is not active. To be considered by Ingeteam too.
|  |  | G01NHA01QZ001-QB20 | XB01 | - | 0 | - | BOOL | -
|  |  | G01NHA01QZ001-QB30 | XB01 | - | 0 | - | BOOL | -
|  |  | G01NHA01QZ001-QB40 | XB01 | - | 0 | - | BOOL | -
| AC_RW2_NC | 3.3 | G01NHA01QZ002-QB10 | XB01 | - | 0 | - | BOOL | - |  | 1oo4 | AC CB Rectifier Row 2 Not ON (not closed) |  |  | N* | N*
|  |  | G01NHA01QZ002-QB20 | XB01 | - | 0 | - | BOOL | -
|  |  | G01NHA01QZ002-QB30 | XB01 | - | 0 | - | BOOL | -
|  |  | G01NHA01QZ002-QB40 | XB01 | - | 0 | - | BOOL | -
| AC_RW1_NO | 3.3 | G01NHA01QZ001-QA10 | GrpErr | - | 1 | - | BOOL | 5 s |  | 1oo4 | AC CB Rectifier Row 1 Feedback Fault Open | AC CBs feedback error (do not open) | [21 empty] | S* | [19 empty] | When AC CBs do not open, if required, the next higher switch (MV CB) is opened. Logic implemented by IGBT controller, too.
|  |  | G01NHA01QZ001-QA20 | GrpErr | - | 1 | - | BOOL
|  |  | G01NHA01QZ001-QA30 | GrpErr | - | 1 | - | BOOL
|  |  | G01NHA01QZ001-QA40 | GrpErr | - | 1 | - | BOOL
| AC_RW2_NO | 3.3 | G01NHA01QZ002-QA10 | GrpErr | - | 1 | - | BOOL | 5 s |  | 1oo4 | AC CB Rectifier Row 2 Feedback Fault Open | [40 empty] | S*
|  |  | G01NHA01QZ002-QA20 | GrpErr | - | 1 | - | BOOL
|  |  | G01NHA01QZ002-QA30 | GrpErr | - | 1 | - | BOOL
|  |  | G01NHA01QZ002-QA40 | GrpErr | - | 1 | - | BOOL
Note on AB17: Mahor, Abhishek (ext): Adapted
Note on AC17: Mahor, Abhishek (ext): Adapted
Note on AB19: Mahor, Abhishek (ext): Adapted
Note on AC19: Mahor, Abhishek (ext): Adapted
Note on AB20: Mahor, Abhishek (ext): Adapted
Note on AB21: Mahor, Abhishek (ext): Adapted
Note on AC21: Mahor, Abhishek (ext): Adapted
Note on AB23: Mahor, Abhishek (ext): Adapted
Note on AC23: Mahor, Abhishek (ext): Adapted
Note on AB24: Mahor, Abhishek (ext): Adapted
Note on AB25: Mahor, Abhishek (ext): Adapted
Note on AB26: Mahor, Abhishek (ext): Adapted
Note on AC26: Mahor, Abhishek (ext): Adapted
Note on AB27: Mahor, Abhishek (ext): Adapted
Note on AB29: Mahor, Abhishek (ext): Adapted
Note on AC29: Mahor, Abhishek (ext): Adapted
Note on AB30: Mahor, Abhishek (ext): Adapted
Note on AC30: Mahor, Abhishek (ext): Adapted
Note on AB31: Mahor, Abhishek (ext): Adapted
Note on AC31: Mahor, Abhishek (ext): Adapted
Note on AB32: Mahor, Abhishek (ext): Adapted
Note on AC32: Mahor, Abhishek (ext): Adapted
Note on AB33: Mahor, Abhishek (ext): Adapted
Note on AC33: Mahor, Abhishek (ext): Adapted
Note on AB34: Mahor, Abhishek (ext): Adapted
Note on AC34: Mahor, Abhishek (ext): Adapted
Note on AB35: Mahor, Abhishek (ext): Adapted
Note on AC35: Mahor, Abhishek (ext): Adapted
Note on AB36: Mahor, Abhishek (ext): Adapted
Note on AC36: Mahor, Abhishek (ext): Adapted
Note on AB37: Mahor, Abhishek (ext): Adapted
Note on AC37: Mahor, Abhishek (ext): Adapted
Note on AB38: Mahor, Abhishek (ext): Adapted
Note on AC38: Mahor, Abhishek (ext): Adapted
Note on AB39: Mahor, Abhishek (ext): Adapted
Note on AC39: Mahor, Abhishek (ext): Adapted
Note on AB40: Mahor, Abhishek (ext): Adapted
Note on AC40: Mahor, Abhishek (ext): Adapted
Note on AB41: Mahor, Abhishek (ext): Adapted
Note on AC41: Mahor, Abhishek (ext): Adapted
Note on AB42: Mahor, Abhishek (ext): Adapted
Note on AC42: Mahor, Abhishek (ext): Adapted
Note on AB43: Mahor, Abhishek (ext): Adapted
Note on AC43: Mahor, Abhishek (ext): Adapted
Note on AB44: Mahor, Abhishek (ext): Adapted
Note on AC44: Mahor, Abhishek (ext): Adapted
Note on AB45: Mahor, Abhishek (ext): Adapted
Note on AC45: Mahor, Abhishek (ext): Adapted
Note on AB46: Mahor, Abhishek (ext): Adapted
Note on AC46: Mahor, Abhishek (ext): Adapted
Note on AB47: Mahor, Abhishek (ext): Adapted
Note on AC47: Mahor, Abhishek (ext): Adapted
Note on AB48: Mahor, Abhishek (ext): Adapted
Note on AC48: Mahor, Abhishek (ext): Adapted
Note on AB49: Mahor, Abhishek (ext): Adapted
Note on AC49: Mahor, Abhishek (ext): Adapted
Note on AB50: Mahor, Abhishek (ext): Adapted
Note on AC50: Mahor, Abhishek (ext): Adapted
Note on AB51: Mahor, Abhishek (ext): Adapted
Note on AC51: Mahor, Abhishek (ext): Adapted
Note on AB52: Mahor, Abhishek (ext): Adapted
Note on AC52: Mahor, Abhishek (ext): Adapted
Note on AB56: Mahor, Abhishek (ext): Adapted
Note on AB70: Mahor, Abhishek (ext): Adapted
Note on AC70: Mahor, Abhishek (ext): Adapted
Note on AB78: Mahor, Abhishek (ext): Adapted
Note on AC78: Mahor, Abhishek (ext): Adapted
Note on AB85: Mahor, Abhishek (ext): Adapted
Note on AC85: Mahor, Abhishek (ext): Adapted
Note on AB87: Mahor, Abhishek (ext):
Note on AB101: Mahor, Abhishek (ext): Adapted
Note on AC101: Mahor, Abhishek (ext): Adapted
Note on AB108: Mahor, Abhishek (ext):
Note on AC108: Mahor, Abhishek (ext):
Note on AB114: Mahor, Abhishek (ext):
Note on AC114: Mahor, Abhishek (ext):
Note on AB116: Mahor, Abhishek (ext): Adapted
Note on AB121: Mahor, Abhishek (ext): Adapted
Note on AB130: Mahor, Abhishek (ext):
Note on AC130: Mahor, Abhishek (ext):
Note on AB131: Mahor, Abhishek (ext):
Note on AC131: Mahor, Abhishek (ext):
Note on AB132: Mahor, Abhishek (ext):
Note on AC132: Mahor, Abhishek (ext):
Note on AB133: Mahor, Abhishek (ext):

## Ely System - Operational
Operational Protection 1 Array - H2 Sakura - has to be adjusted project specifically - S --> storing, reset required / speichernd, rücksetzen erforderlich N --> non storing, no reset required / nicht speichernd, rücksetzen nicht erforderlich NP--> non storing purge, reset when purge is finished or canceled / nicht speichernde Spülung, Rücksetzen wenn Spülung beendet oder abgebrochen | [16 empty] | Effect Description | Rectifier 1 OFF (immediate Customer's scope | Rectifier 2 OFF (immediate) Customer's scope | Rectifier 3 OFF (immediate) Customer's scope | Rectifier 4 OFF (immediate) Customer's scope | Rectifier 1 OFF (ramp down) 3) Customer's scope | Rectifier 2 OFF (ramp down) 3) Customer's scope | Rectifier 3 OFF (ramp down) 3) Customer's scope | Rectifier 4 OFF (ramp down) 3) Customer's scope | Discharge resistor 1 (Scope to be calrified) | Discharge resistor 2 (Scope to be calrified) | Discharge resistor 3 (Scope to be calrified) | Discharge resistor 4 (Scope to be calrified) | N2 Purging H2&O2 side | Controlled N2 Purging H2 side | Compressor Trip | H2 Product Valve | Array - Inert required | Array - H2 ready | Demin Supply Valve | Rectifier Cooling Pump | Water Refinement Pump | Buffer 4) Tank - Set Inert required | Buffer 4) Tank - Reset H2 ready | Gas Analytic H2 | Gas Analytic O2 | Trafo Oil Pump Customer's scope | MV Circuit Breaker 2) (Customer's scope) | Tap changer 1) | OPTIONAL: Only for IGBT Rectifier | Tap changer 1) | DC Disconnectors Rectifier Row 1&2 |  |  |  | DC Disconnectors Rectifier Row 1&2 |  |  |  | AC Circuit Breakers Row 1 | AC Circuit Breakers Row 2 | MV Circuit Breaker 2) | Load reduction to 40 % | 1) Tap Changer is pulse controlled (0->1) 2) MV Circuit Breaker is located in Medium Voltage Supply (=T01), but controlled by Rectifier System of Array. Tag is different for each Array (e.g. T01BBA01QA004/5/6-QA01 for Array 1/2/3) 3) Ramp down to 3000A with 750A/s, then ramp down to 0A with 375A/s 4) There is no specific constant pressure piston buffer tank in H2 Sakura project downstream of product control valve. Hence customer's contant volume tank to be reffered as buffer tank/volume
[17 empty] | Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 |  | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | Output Tag | =G01NHA01TB001-KF01;YQ02 | =G01NHA01TB002-KF01;YQ02 | =G01NHA01TB003-KF01;YQ02 | =G01NHA01TB004-KF01;YQ02 | =G01NHA01TB001-KF01;YQ01 | =G01NHA01TB002-KF01;YQ01 | =G01NHA01TB003-KF01;YQ01 | =G01NHA01TB004-KF01;YQ01 | =G01NHA01RA001-KF01;YB11 | =G01NHA01RA002-KF01;YB11 | =G01NHA01RA003-KF01;YB11 | =G01NHA01RA004-KF01;YB11 | =G01NHX01KF201/KZ00 | =G01NHX01QN001-QN01 | =G01NHY01KF001-KZ65;YB31 | =G01NHC01GT001-QN01;YQ01 | =G01NHY01KF101/KZ103 | =G01NHY01KF101/KZ100 | =G01NHG01QM001-QM01;YB31 | =G01NHA01EQ001-GP01;YB21 =G01NHA01EQ001-GP02;YB21 | =G01NHH01HP001-GP01;YV01 | =G01NHY01KF102;YV01 | =G01NHY01KF102;YV02 | =GnyNHC01KF202/KZ02 | =GnyNHE01KF202/KZ02 | =G01NHA01TA001-GP01;YB11 =G01NHA01TA001-GP02;YB11 | =T01BBA01QA00x-QA01;YW01 | =G01NHA01TA001-QA02;YB22 |  | =G01NHA01TA002-QA02;YB22 | =G01NHA01QZ001-QA12;YB12 | =G01NHA01QZ001-QA32;YB12 | =G01NHA01QZ002-QA12;YB12 | =G01NHA01QZ002-QA32;YB12 | =G01NHA01QZ001-QA12;YB12 '=G01NHA01QZ001-QA13;YB12 | =G01NHA01QZ001-QA32;YB12 =G01NHA01QZ001-QA33;YB12 | =G01NHA01QZ002-QA12;YB12 =G01NHA01QZ002-QA13;YB12 | =G01NHA01QZ002-QA33;YB12 =G01NHA01QZ002-QA32;YB12 | =G01NHA01KF201-/KZ31 | =G01NHA01KF201-/KZ32 | =T01BBA01QA00x-QA02;YW01 | =T01BBA01QA00x-QA01;YW01 |  | INTERNAL: 'V3.3: Columns for Rectifier 3 & 4, "trafo oil pump" and column "rect. Cooling pump" are only applicable for thyristor based rectifier system. Rectifier OFF shall trigger the shut down sequence of rectifiers incl. opening of all AC circuit breakers (by Ingeteam). |  | V3.0: , BM, 8.11.2023; Signal for Refinment pump changed from "YB21" to "YV01" V3.3: BM, 6.11.2024: N2 Purge step sequence changed from "...KF101..." to ...KF201/KZ00"
[17 empty] | Action | off | off | off | off | off | off | off | off | off | off | off | off | start | start | on | close | on | off | close | off | off | on | off | off | off | off | open | off |  | off | Not open | Not open | Not open | Not open | Not closing | Not closing | Not closing | Not closing | open | open | open | open
PLS# | Identifier | Project Rev. | Chgd | Input Tag | Signal | Warn | Switch/Limit | Hyst. | Unit | W_DC | A_DC | A_DG | Func 1 | Func 2 | Cause Description | Comment | [43 empty] | Comments, Causes / Kommentare, Ursachen | Test date/result | Test executed by | Revision history /internal comments
Balance of Plant (BoP) | [59 empty] | Warning: Country specific requirements DE: separation is required.
| Ckd by SG Found Ok | A | 3.3 | G01NHY01KF101-KZ81 | XM01 | - | 1 | - | BOOL | - | 5 s | - |  | 1oo1 | Communication fault with BoP | Lifebit freezed | [5 empty] | N | N | N | N |  |  |  |  | NP |  |  | N | S |  | N | [23 empty] | If communication to BoP is lost, then the array must shut down and go to safe state. If reset is required, this shall be implemented in the higher level system | 24.04.2025 implemented change | F.Reinhart | V1.4 (FR): added communication with BoP V2.0 (JS, FR, RW, FH): OPTIONAL: only H2 side shall be purged since all arrays are purged at the same time (software not yet implemented) V3.1 (BM, KB): Inter required status shall be set V3.2, BM, FR, 2024.05.15: first line deleted (signal "0") , NHY01KF102-KZ01 changed to KF101-KZ81 V3.3, BM+FR, 2025-04-22: changed S to N, because reset shall be done in higher level system
Check and OK by AS 22042026 | Ckd by SG Connection not found with effect | A | 3.3 | G01NHY01KF101-KZ75 | XV01 | - | 0 | - | BOOL | - | - | - |  | 1oo1 | Array Trip (from BoP) | via AS-AS communication | [5 empty] | N | N | N | N | [6 empty] | N | N | [26 empty] | If reset is required, this shall be implemented in the higher level system | 24.04.2025 implemented change | F.Reinhart | V1.4 (FR): added communication with BoP V3.2, BM, FR, 2024.05.15: first line deleted (signal "0") , NHY01KF102-KZ01 changed to KF101-KZ75 V3.3, BM+FR, 2025-04-22: changed S to N, because reset shall be done in higher level system
Check and OK by AS 22042026 | Ckd by SG Connection not found with effect | A | 3.3 | G01NHY01KF101-KZ77 | XV01 | - | 0 | - | BOOL | - | - | - |  | 1oo1 | Array Trip with N2 Purge (from BoP) | via AS-AS communication | [5 empty] | N | N | N | N |  |  |  |  | NP |  | N | N | S | [25 empty] | During N2 Purge the Rectifiers must also be shutdown to reach a safe inerted state. If reset is required, this shall be implemented in the higher level system | 24.04.2025 implemented change | F.Reinhart | V1.4 (FR): added communication with BoP V2.0 (JS, FR, RW, FH): OPTIONAL: only H2 side shall be purged since all arrays are purged at the same time (software not yet implemented) V3.1 (BM, KB): Inter required status shall be set V3.2, BM, FR, 2024.05.15: NHY01KF102-KZ03 changed to KF101-KZ77 XV01 V3.3, BM+FR, 2025-04-22: changed S to N, because reset shall be done in higher level system
| Found Ok | A | 3.2 | G01NHY01KF101-KZ78 | XV01 | - | 0 | - | BOOL | - | - | - |  | 1oo1 | No Product Gas Release (from BoP) | via AS-AS communication, no message | [15 empty] | N | N | [26 empty] | The product gas release will control the product valve, when no other interlock or protection signals of the electrolyzer are active. | 24.04.2025 implemented change | F.Reinhart | V1.4 (FR): added communication with BoP V3.2, BM, FR, 2024.05.15: NHY01KF102 changed to KF101-KZ78 XV01
| Found Ok | A | 3.3 | G01NHY01KF101-KZ79 | XV01 | - | 0 | - | BOOL | - | - | - |  | 1oo1 | Close Demin Supply Valve (from BoP) | via AS-AS communication, no message | [19 empty] | N | [23 empty] | If reset is required, this shall be implemented in the higher level system | 24.04.2025 implemented change | F.Reinhart | V1.4 (FR): added communication with BoP V3.2, BM, FR, 2024.05.15: NHY01KF102 changed to KF101-KZ79 XV01 V3.3, BM+FR, 2025-04-22: changed S to N, because reset shall be done in higher level system
Gas Analytic H2 side - NHC01BQ001-BQ01(discont.)
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHC01BQ001-BQ01 | XQ01 | - | AH 4500 | 4000 | ppmV | - | - | - | and | 1oo2 | Concentration - Gas analytic H2 - High limit during shutdown | Concentration of sensor 1 | [14 empty] | N | N | N |  | S | [24 empty] | - during shutdown the foreign gas concentration can rise due to level shifts via the water refinement - operational limits use the saved gas concentrations instead of the actual measurement value | 28.04.2025 implemented change | F.Reinhart | 09.03.2023 FR+BM '- during shutdown the foreign gas concentration can rise due to level shifts via the water refinement - controlled nitrogen purge to keep foreign gas concentration low during shutdown - trip value must be lower to the trip value during operation, so that no trip during startup can occur V3.1 FR+RW+KB 26.01.2024 - Note: The stored value is used for the operational switch-off and not the actual measured value. V3.1, 2024-03-04 (BM+FR): "G01NHY01KF101-KZ11" changed to "G01NHY01KF101/KZ12;XB01" V3.2, FR,JS,RW,BM, 2024-07-02: calibration mode, sensor fault and bad signal deleted and replaced by common signal of S1 and S2 "GA_not ready" which is generated in SIS part V3.3, BM, 2025.03.18: ASH, and ASHH
|  | A |  | GA_H2_S1_NOT_RDY |  | - | 1 | - | BOOL | - | - | - |  |  |  | 1 = GA H2 S1 ready
|  | A |  | G01NHY01KF101/KZ12 | XB01 | - | 0 | - | BOOL | - | - | - |  |  |  | 0= Array not in operation
|  | A |  | G01NHC01BQ001-BQ02 | XQ01 | - | AH 4500 | 4000 | ppmV | - | - | - | and |  |  | Concentration of sensor 2
|  | A |  | GA_H2_S2_NOT_RDY |  | - | 1 | - | BOOL | - | - | - |  |  |  | 1 = GA H2 S2 ready
|  | A |  | G01NHY01KF101/KZ12 | XB01 | - | 0 | - | BOOL | - | - | - |  |  |  | 0= Array not in operation
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHC01BQ001-BQ01 | XQ01 | AH 4500 | AHH 5000 | 4000 | ppmV | - | - | - | and | 1oo2 | Concentration - Gas analytic H2 - High limit during operation | Concentration of sensor 1 | [5 empty] | S | S | S | S | [6 empty] | S | S | [26 empty] | - adjust based on downstream systems. Deoxo needs a trip value of e.g. 5000 ppm (to be clarified if SIS or operational). Otherwise higher values are possible, e.g. 8000 ppm - For multiarray plants it is recommended to consider an additional foreign gas measurement upstream of buffer tank to measure average gas concentration of all arrays. In this case a trip value of 8000 ppm is possible, because Deoxo is protected by corresponding foreign gas measurement. - operational limits use the saved gas concentrations instead of the actual measurement value | 28.04.2025 implemented change | F.Reinhart | V1.4 If a SIS limit for Deoxo is considered anyway, this value can be 8.000 ppm. If a operational trip for deoxo protection is sufficient a corresponding value shall be used for this trip (e.g. 5.000 ppm). V3.1, 2024-03-04 (BM+FR): "G01NHY01KF101-KZ11" changed to "G01NHY01KF101/KZ12;XB01" V3.2, FR,JS,RW,BM, 2024-07-02: calibration mode, sensor fault and bad signal deleted and replaced by common signal of S1 and S2 "GA_not ready" which is generated in SIS part V3.3, BM, 2025.03.18: ASH, and ASHH
|  | A |  | GA_H2_S1_NOT_RDY |  | - | 1 | - | BOOL | - | - | - |  |  |  | 1 = GA H2 S1 ready
|  | A |  | G01NHY01KF101/KZ12 | XB01 | - | 1 | - | BOOL | - | - | - |  |  |  | 1= Array in operation
|  | A |  | G01NHC01BQ001-BQ02 | XQ01 | AH 4500 | AHH 5000 | 4000 | ppmV | - | - | - | and |  |  | Concentration of sensor 2
|  | A |  | GA_H2_S2_NOT_RDY |  | - | 1 | - | BOOL | - | - | - |  |  |  | 1 = GA H2 S2 ready
|  | A |  | G01NHY01KF101/KZ12 | XB01 | - | 1 | - | BOOL | - | - | - |  |  |  | 1= Array in operation
| Ckd by SG Connection not found with effect | A | 3.3 | Concentration - Gas analytic H2 - High limit during shutdown |  | - | 1 | - | BOOL | - | 10 s | - | or | and | Concentration - Gas analytic H2 - High limit and product valve not closed | [23 empty] | S | [20 empty] | If Product gas valve NHC01GT001-QN01 does not close within 10 s, the status of "no inert required" for buffer tank is reset. Indicate cause via message of product valve. | 29.04.2025 implemented change | F.Reinhart | V3.3, 2025-04-29 (FR): changed comment, indicate cause via message of product valve
|  | A |  | Concentration - Gas analytic H2 - High limit during operation |  | - | 1 | - | BOOL | - |  | -
|  | A |  | G01NHC01GT001-QN01/VLV | XB02 | - | 0 | - | BOOL | - | - | -
| Ckd by SG Connection not found with effect | A | 3.2 | G01NHC01KF202/KZ00 | S_ERRG | - | 1 |  | BOOL | - | - | - |  | 1oo3 | Gas analytic H2 - not ready | 1 = Step error (H2 Gas Analytic sequence) | [5 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | Change implemenred 18.03.2025 | P.Kumar | 09.03.2023 FR+BM+RW - removed delay of 72 h for sensor drift to prevent operation of electrolyzer with invalid measurement - instead warning limit to allow operator to mitigate sensor drift before shutdown - polarization rectifier must be tripped, because there is no valid measurement of concentration 18.04.2024: BM: pol rect comments deleted; step sequence "error" and "step sequence ready" added. Step sequence ready means, that all sampling valves / full cycle of array separators has be measured once. V3.2, BM, JS, FR, RW, 2024-07-02: sensor drift deleted and shifted to SIS; calibration mode, sensor fault and bad signal replaced by common fault of S1 and S2 since covered by "GA_not ready" which is generated in SIS part
|  | A |  | G01NHC01KF202/KZ00 | Q_READY | - | 0 |  | BOOL | - | - | - |  |  |  | 0 = Not ready (H2 Gas Analytic sequence)
|  | A |  | GA_H2_S1_NOT_RDY |  | - | 0 | - | BOOL | - | - | - | and |  |  | 0 = GA H2 S1 not ready
|  | A |  | GA_H2_S2_NOT_RDY |  | - | 0 | - | BOOL | - | - | - |  |  |  | 0 = GA H2 S2 not ready
Gas Analytic O2 side - NHE01BQ001-BQ01 (discont.)
| Ckd by SG Connection not found with effect | A | 3.2 | G01NHE01BQ001-BQ01 | XQ01 | AH 1.8 | ASHH 1.9 | 1.4 | Vol % | - | - | - | and | 1oo2 | Concentration - Gas analytic O2 - High limit | Concentration of sensor 1 | [5 empty] | S | S | S | S |  |  |  |  | NP |  | S | S | S | [25 empty] | - INFO: Measurement deviation with 95 Vol-% of N2 content on O2 side is approx. 2,06 Vol-% for H2 in N2. An automated measurement offset is not considered. - operational limits use the saved gas concentrations instead of the actual measurement value | Change implemenred 18.03.2025 | P.Kumar | V3.1 (BM, KB), 8.1.2024: when inertisation is triggered, operation of polrect is not possible (see "Array inert required '=G01NHB01KF201;XA02") V3.1 FR+RW+KB 26.01.2024 - Note: The stored value is used for the operational switch-off and not the actual measured value. V3.2, FR,JS,RW,BM, 2024-07-02: calibration mode, sensor fault and bad signal deleted and replaced by common signal of S1 and S2 "GA_not ready" which is generated in SIS part
|  | A |  | GA_O2_S1_NOT_RDY |  | - | 1 | - | BOOL | - | - | - |  |  |  | 1 = GA O2 S1 ready
|  | A |  | G01NHE01BQ001-BQ02 | XQ01 | AH 1.8 | ASHH 1.9 | 1.4 | Vol % | - | - | - | and |  |  | Concentration of sensor 2
|  | A |  | GA_O2_S2_NOT_RDY |  | - | 1 | - | BOOL | - | - | - |  |  |  | 1 = GA O2 S2 ready
| Ckd by SG Connection not found with effect | A | 3.2 | G01NHE01KF202/KZ00 | S_ERRG | - | 1 | - | BOOL | - | - | - |  | 1oo3 | Gas analytic O2 - not ready | 1 = Step error (O2 Gas Analytic sequence) | [5 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | "Change implemenred 18.03.2025" | P.Kumar | 09.03.2023 FR+BM+RW - removed delay of 72 h for sensor drift to prevent operation of electrolyzer with invalid measurement - instead warning limit to allow operator to mitigate sensor drift before shutdown - polarization rectifier must be tripped, because there is no valid measurement of concentration 18.04.2024: BM: pol rect comments deleted; step sequence "error" and "step sequence ready" added. Step sequence ready means, that all sampling valves / full cycle of array separators has be measured once. V3.2, FR,JS,RW,BM, 2024-07-02: calibration mode, sensor fault and bad signal deleted and replaced by common signal of S1 and S2 "GA_not ready" which is generated in SIS part
|  | A |  | G01NHE01KF202/KZ00 | Q_READY | - | 0 | - | BOOL | - | - | - |  |  |  | 0 = Not ready (O2 Gas Analytic sequence)
|  | A |  | GA_O2_S1_NOT_RDY |  | - | 0 | - | BOOL | - | - | - | and |  |  | 0 = GA O2 S1 not ready
|  | A |  | GA_O2_S2_NOT_RDY |  | - | 0 | - | BOOL | - | - | - |  |  |  | 0 = GA O2 S2 not ready
Gas Separation
| Ckd by PM | A | 1.3 | G01NHC01BL001-BL02 | XQ01 | AH 40.0 | ASHH 42.0 | 1.0 | cm | - | - | - |  | 1oo2 | Gas Separator Level Max | [6 empty] | S | S | S | S | [6 empty] | S | S |  |  | N | [23 empty] | 0 cm equal to bottom of Separator | 28.04.2025 no change | F. Reinhart | V1.4 (FR): do not switch off demin water pump, it's enough to close the supply valve (especially relevant for multi array)
|  | A |  | G01NHE01BL001-BL02 | XQ01 |  |  |  |  | -
| Ckd by PM | A | 3.3 | G01NHC01BL001-BL02 | XQ01 | AL (Note 1) | ASLL (Note 1) | 1.0 | cm | - | 3 min | - |  | 1oo2 | Gas Separator Level Min | [6 empty] | S | S | S | S | [6 empty] | S | S | [26 empty] | Note 1: depending on electrolyzer load (sum of rect. current) a variable limit is set: warning: min 13,2 cm / trip: min 12,2 cm | 28.04.2025 implemented change | F. Reinhart | V3.0, BM, 24.10.2023: fix of mistake, Cell AT74: values were changed from 8/9 cm to 12,2/13,2 cm V3.3, 25.04.2025, FR+BM: variable limit was adjusted (see tab var. level limits)
|  | A |  | G01NHE01BL001-BL02 | XQ01 |  |  |  |  | -
| Ckd by PM | A | 3.3 | G01NHC01HP001-BP02 | XQ01 | AL 15.0 | ASLL 10.0 | 5.0 | mbar(g) | 30 s | 1 min | - |  | 1oo1 | Underpressure Monitoring H2 Side | [6 empty] | S | S | S | S | [6 empty] | S | S | S | S | [25 empty] | 28.04.2025 no change | F. Reinhart | V2.0: 2023-08-29 (JW, FR, BM, RW): Betriebliche Verriegelung der Gleichrichter hizugefügt. V2.0: 2023-08-31 (JS, BM): "inert required" mit S gesetzt, um Fehlerfall "offenes Abblaseventil" mit abzudecken V3.1 (BM, KB), 8.1.2024: when inertisation is triggered, operation of polrect is not possible (see "Array inert required '=G01NHB01KF201;XA02") V3.1,V2.1 2024-01-23 (KB,FR): Delay Time for Warning changed (complete new column inserted) V3.3, BM, FR, JS: Increase of trip value from 5 to 10 mbarg to cover measurement uncertainty. warning also increased from 10 to 15 mbarg.
|  |  | 3.3_200 | GnyNHC01HP001-BP02 | XQ01 | - | ASLLL -5.0 | 5.0 | mbar(g) | - | 1 min | - |  | 1oo1 | Vacuum Protection H2 Side | in case of sensor fault use BP01 as substitute value | [24 empty] | N | N | [17 empty] | When the blowoff valves are closed and the pressure hold with N2 does not work, the Gas Analytic can cause a vacuum in the system (for which it is not designed). When only one Gas Analytic is running or when N2 is only injected on one side (due to a fault), this can also lead to high differential pressure with according level shift. -> Gas Analytic shall be shut down, when vacuum is detected.
|  |  | 3.3_200 | GnyNHE01HP001-BP02 | XQ01 | - | ASLLL -5.0 | 5.0 | mbar(g) | - | 1 min | - |  | 1oo1 | Vacuum Protection O2 Side | in case of sensor fault use BP01 as substitute value | [24 empty] | N | N
| Ckd by PM | A | 2.0 | G01NHC01GT001-QN01/VLV | XB02 | 0 | 0 |  | BOOL | - | 1 min |  |  | 2oo2 | Blow off valve and Product Gas Valve open at same time on H2 side | Check back closed | [5 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 no change | F. Reinhart | V2.0: 20230829 (JW, FR, BM, RW): Hinzugefügt. Fehlerhaftes Öffnen des Abblaseventils (H2)-> Produktgasventil soll schließen
|  | A |  | G01NHC01GT001-QN02/VLV | XB02 | 0 | 0 |  | BOOL | - | [5 empty] | Check back closed
Module Temperatures
Check and OK by AS 22042026 | Ckd by SG Connection not found with effect | A | 3.3 | G01NHB01HT001-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. High Outlet Stack 1 / Group 1 | [6 empty] | S | S | S | S | [6 empty] | S | S | [26 empty] | after 5min of >100A of rectifier no action upon 1 detected sensor fault (1oo2SR), alarm only enabled, when according row is enabled (warning remains enabled even when row is disabled) | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB01HT001-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB01HT002-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 2 / Group 1 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB01HT002-BT02 | XQ01 | [16 empty] | S | S | S | S | [37 empty] | V.3.2: BM, 26.04.2024: "after 5min of >100A of rectifier no action upon 1 detected sensor fault (1oo2SR)" updated with (1oo2SR) selective redundancy and shifted to comments V3.3, FR, 25.03.2025: alarm only enabled, when according row is enabled (warning remains enabled even when row is disabled), replaced S1/S2 with S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB01HT003-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 3 / Group 1 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB01HT003-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB01HT004-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 4 / Group 1 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB01HT004-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB02HT001-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 1 / Group 2 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB02HT001-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB02HT002-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 2 / Group 2 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB02HT002-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB02HT003-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 3 / Group 2 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB02HT003-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB02HT004-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 4 / Group 2 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB02HT004-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB03HT001-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 1 / Group 3 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB03HT001-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB03HT002-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 2 / Group 3 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB03HT002-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB03HT003-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 3 / Group 3 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB03HT003-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB03HT004-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 4 / Group 3 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB03HT004-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB04HT001-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 1 / Group 4 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB04HT001-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB04HT002-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 2 / Group 4 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB04HT002-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB04HT003-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 3 / Group 4 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB04HT003-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB04HT004-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 4 / Group 4 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB04HT004-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB05HT001-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 1 / Group 5 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB05HT001-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB05HT002-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 2 / Group 5 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB05HT002-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB05HT003-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 3 / Group 5 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB05HT003-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB05HT004-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 4 / Group 5 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB05HT004-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB06HT001-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 1 / Group 6 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB06HT001-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB06HT002-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 2 / Group 6 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB06HT002-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB06HT003-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 3 / Group 6 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB06HT003-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Connection not found with effect | A | 3.3 | G01NHB06HT004-BT01 | XQ01 | AH 68.0 | ASHH 70.0 | 1.0 | °C | - | 5 s | - |  | 1oo2 | Temp. outlet Stack 4 / Group 6 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHB06HT004-BT02 | XQ01 | [16 empty] | S | S | S | S
| Ckd by SG Found Ok | A | 1.1 | G01NHB01EQ001-BQ01 | XQ02 | AL 5.0 | ASLL 4.0 | 1.0 | °C | - | 5 min | - |  | 2oo2 | Temp. Low Stack Group 1 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 no change | F. Reinhart | Abschaltung ggf überdenken
|  | A | 1.1 | G01NHB01EQ001-BQ02 | XQ02 |  | L 4.0 | 1.0 | °C |  | 5 min | - |  |  | Temp. min Modules H2 Group 1 | [47 empty] | Abschaltung ggf überdenken
| Ckd by SG Found Ok | A | 1.1 | G01NHB02EQ001-BQ01 | XQ02 | AL 5.0 | ASLL 4.0 | 1.0 | °C | - | 5 min | - |  | 2oo2 | Temp. min Stack Group 2 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 no change | F. Reinhart | Abschaltung ggf überdenken
|  | A | 1.1 | G01NHB02EQ001-BQ02 | XQ02 |  | L 4.0 | 1.0 | °C |  | 5 min | - |  |  | Temp. min Modules H2 Group 2 | [47 empty] | Abschaltung ggf überdenken
| Ckd by SG Found Ok | A | 1.1 | G01NHB03EQ001-BQ01 | XQ02 | AL 5.0 | ASLL 4.0 | 1.0 | °C | - | 5 min | - |  | 2oo2 | Temp. min Stack Group 3 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 no change | F. Reinhart | Abschaltung ggf überdenken
|  | A | 1.1 | G01NHB03EQ001-BQ02 | XQ02 |  | L 4.0 | 1.0 | °C |  | 5 min | - |  |  | Temp. min Modules H2 Group 3 | [47 empty] | Abschaltung ggf überdenken
| Ckd by SG Found Ok | A | 1.1 | G01NHB04EQ001-BQ01 | XQ02 | AL 5.0 | ASLL 4.0 | 1.0 | °C | - | 5 min | - |  | 2oo2 | Temp. min Stack Group 4 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 no change | F. Reinhart | Abschaltung ggf überdenken
|  | A | 1.1 | G01NHB04EQ001-BQ02 | XQ02 |  | L 4.0 | 1.0 | °C |  | 5 min | - |  |  | Temp. min Modules H2 Group 4 | [47 empty] | Abschaltung ggf überdenken
| Ckd by SG Found Ok | A | 1.1 | G01NHB05EQ001-BQ01 | XQ02 | AL 5.0 | ASLL 4.0 | 1.0 | °C | - | 5 min |  |  | 2oo2 | Temp. min Stack Group 5 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 no change | F. Reinhart
|  | A | 1.1 | G01NHB05EQ001-BQ02 | XQ02 |  | L 4.0 | 1.0 | °C |  | 5 min | - |  |  | Temp. min Modules H2 Group 5
| Ckd by SG Found Ok | A | 1.1 | G01NHB06EQ001-BQ01 | XQ02 | AL 5.0 | ASLL 4.0 | 1.0 | °C | - | 5 min | - |  | 2oo2 | Temp. min Stack Group 6 | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 28.04.2025 no change | F. Reinhart
|  | A | 1.1 | G01NHB06EQ001-BQ02 | XQ02 |  | L 4.0 | 1.0 | °C |  | 5 min | - |  |  | Temp. min Modules H2 Group 6
Stack Voltage (only in case of stack voltage measurement On the basis of total calculated cell voltage )
PN/PN (CVM) | Ckd by SG Not found this tag | A | 3.3 | G01NHB01KF002-BA01 | XQ01 | AH 115 | (ASHH 120.0) | 0.1 | V | 15 s | 30 s | - |  | 1oo1 | Stack voltage high | [6 empty] | S | S | S | S | [6 empty] | S | S | [26 empty] | TRIP only optional Warning and optional trip is only active when electrolyer is in operation (> 100 A) Voltage trips are only active, if respective row is in operation & enabled. | "No Change required 19.03.2025" | P.Kumar | V1.4: Alternative zur Einzelzellspannungsmessung Abschaltung wurde wieder eingefügt, da zuverlässiger als Einzelzellspannungsmessung. Ggf. kann bei Ausfall einer Stackspannungsmessung ein Ersatzwert gebildet werden: Reihenspannung - Summe der anderen Stackspannungen V2.0, 2023-10-09: Nach Rücksprache mit Th. Bäzner: Trip nur optional und nicht verpflichtend. V3.0, BM, 24.10.2023: Tag no changed from G01...KF001.... to G01....KF002..... V3.3, BM, FR, 2024-11-15: delay coming for warning low and high added. V3.3, BM, FR, 2024.11.25: added: "Voltage trips are only active, if respective row is in operation."
| Ckd by SG Not found this tag | A | 3.3 | G01NHB01KF002-BA01 | XQ01 | AL 75 | (ASLL 72,5) | 0.1 | V | 15 s | 30 s | - |  | 1oo1 | Stack voltage low | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | "No Change required 19.03.2025" | P.Kumar
| Ckd by SG Not found this tag | A | 3.3 | G01NHB01KF002-BA02 | XQ01 | AH 115 | (ASHH 120.0) | 0.1 | V | 15 s | 30 s | - |  | 1oo1 | Stack voltage high | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | "No Change required 19.03.2025" | P.Kumar
| Ckd by SG Not found this tag | A | 3.3 | G01NHB01KF002-BA02 | XQ01 | AL 75 | (ASLL 72,5) | 0.1 | V | 15 s | 30 s | - |  | 1oo1 | Stack voltage low | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | "No Change required 19.03.2025" | P.Kumar
| Ckd by SG Not found this tag | A | 3.3 | G01NHB01KF002-BA03 | XQ01 | AH 115 | (ASHH 120.0) | 0.1 | V | 15 s | 30 s | - |  | 1oo1 | Stack voltage high | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | "No Change required 19.03.2025" | P.Kumar
| Ckd by SG Not found this tag | A | 3.3 | G01NHB01KF002-BA03 | XQ01 | AL 75 | (ASLL 72,5) | 0.1 | V | 15 s | 30 s | - |  | 1oo1 | Stack voltage low | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | "No Change required 19.03.2025" | P.Kumar
| Ckd by SG Not found this tag | A | 3.3 | G01NHB01KF002-BA04 | XQ01 | AH 115 | (ASHH 120.0) | 0.1 | V | 15 s | 30 s | - |  | 1oo1 | Stack voltage high | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | "No Change required 19.03.2025" | P.Kumar
| Ckd by SG Not found this tag | A | 3.3 | G01NHB01KF002-BA04 | XQ01 | AL 75 | (ASLL 72,5) | 0.1 | V | 15 s | 30 s | - |  | 1oo1 | Stack voltage low | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | "No Change required 19.03.2025" | P.Kumar
|  | A | 3.3 | … | XQ01 | AH 115 | (ASHH 120.0) | 0.1 | V | 15 s | 30 s | - |  | 1oo1 | Stack voltage high | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | "No Change required 19.03.2025" | P.Kumar
|  | A | 3.3 | … | XQ01 | AL 75 | (ASLL 72,5) | 0.1 | V | 15 s | 30 s | - |  | 1oo1 | Stack voltage low | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | "No Change required 19.03.2025" | P.Kumar
| Ckd by SG Not found this tag | A | 3.3 | G01NHB06KF002-BA04 | XQ01 | AH 115 | (ASHH 120.0) | 0.1 | V | 15 s | 30 s | - |  | 1oo1 | Stack voltage high | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | "No Change required 19.03.2025" | P.Kumar
| Ckd by SG Not found this tag | A | 3.3 | G01NHB06KF002-BA04 | XQ01 | AL 75 | (ASLL 72,5) | 0.1 | V | 15 s | 30 s | - |  | 1oo1 | Stack voltage low | [6 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | "No Change required 19.03.2025" | P.Kumar
Water Refinement
| Ckd by PM | A | 3.3 | G01NHH01HP001-BF01 | XQ01 | AL (SP-20%) | ASLL (SP-30%) | 1.0 | m³/h | 30 s | 30 s | - |  | 1oo1 | Minflow Protection Pump (low flow) | minimum warning/trip limit 4.4/4.0 m³/h | [21 empty] | S | [21 empty] | project specific, rectifier shall be ramped down with different time delay (5 min) The warning/trip limit shall be limited to minimum 4 m³/h (tbc by selected pump) to protect the pump, when the setpoint is controlled by operator in manual/external mode. | 28.04.2025 implemented change | F. Reinhart | V1.4 (FR): fix hysteresis, no need for percent of SP V3.0 (KB, BM), 17.10.2023: Ramp down of rectifiers included, since there is no sense in operating the electrolyzer for longer periods without refinement. There would only be the isolation monitoring to shut down in case of stopped refinement unit. V3.0(KB),07.11.23: Refinement Pump shutdown and rectifier ramp down separated into different rows V3.2, BM, 2024-07-03: comment to trip value in manual mode added V3.3, BM+FR, 2025-04-28: limit warning/trip limit to 4.4/4.0 m³/h independent of pump or controller mode
| Ckd by PM | A | 3.3 | G01NHH01HP001-QN01 | CtrlError | - | 1 | - | bool | - | 30 s | - |  | 1oo1 | Control Error- Water Refinement Control Valve | Valve position set value and feedback differ too much (2%) | [21 empty] | S | [22 empty] | Change implemented 20.03.2025 | P.Kumar | V3.0(KB),07.11.23: Refinement Pump shutdown and rectifier ramp down separated into different rows V3.3., KB; BM, 15.07.2024: Abweichung von 10 auf 2% geändert (Software: MonTiDynamic=30 sec; PosDeadB=2.0)
Check and OK by AS 27042026 | NOT working | A | 3.0 | G01NHY01KF101/KZ12 | XB01 | - | 1 | - | bool | - | 5 min | - | and | 1oo1 | 1=Array in Operation | [6 empty] | S | S | S | S | [6 empty] | S | S | [26 empty] | When the Waterrefinement pump is not running, while Array is in Operation. Message for this is included in the pump typical | 28.04.2025 no change | F. Reinhart | V3.0(KB),07.11.23: Refinement Pump shutdown and rectifier ramp down separated into different rows
|  | A |  | G01NHH01HP001-GP01 | XG01 | - | 0 | - | bool |  |  | - |  |  | Water Ref Pump Fbk Off | [22 empty] | N | [21 empty] | rectifier shall be ramped down with different time delay (5 min) |  |  | V3.0 (KB, BM), 17.10.2023: Ramp down of rectifiers included, since there is no sense in operating the electrolyzer for longer periods without refinement. There would only be the isolation monitoring to shut down in case of stopped refinement unit.
| TOC measurement | A
N2 Supply
| Ckd by PM | A | 1.1 | G01NHX01QN001-BP01 | XQ01 | AL 1.2 | ASLL 1.0 | 0.2 | bar(g) | - | - | 60 s |  | 2oo2 | N2 Supply Pressure too low | [6 empty] | S | S | S | S | [6 empty] | S | S | [26 empty] | project specific, if there is a sudden loss of nitrogen it might be better to keep array in operation, because the array needs nitrogen by N2 skid if the array is shut down (preesure hold on O2 side). Blow off lances of H2 need to avoid ingress of air if array shuts down (blanketed lances). | 25.04.2025 no change | F. Reinhart
|  | A |  | G01NHX01QN002-BP01 | XQ01 | L 1.2 | L 1.0 | 0.2 | bar(g) |  | - | 60 s |  |  | N2 Supply Separator/Header | [7 empty] | S | S | S | [6 empty] | S | S | [26 empty] | project specific
| Ckd by PM | A | 3.2 | G01NHX01QN001-QN01/VLV | XB02 | - | 0 | - | BOOL | - | 1 s | - | and | 1oo2 | N2 To H2 Side | no messages for this cause | [18 empty] | S | [25 empty] | 28.04.2025 no change | F. Reinhart | V1.4 (FR): removed protect of product valve, because product valve is interlocked, when H2 ready is reset V2.0, 2023-08-31, (JS, BM, RW): Rectifier shut down in "N" to cover loss of instrument air and preventing continious blow off of H2 to atmosphere. V3.1, 2024-01-26 (BM,FR): Removed "N" from rectifier shutdown to avoid unintended interlock of rectifier during normal operational pressure holding (at standby). Therefore separate, new cause for rectifier shutdown during operation (see below). V3.2, 2024-04-04, BM: Effect corrected. "S" for "H2 ready" not for "demin supply valve"
|  | A |  | G01NHX01QN001-QM21 (QM05) | XB02 | - | 0 | - | BOOL | - | 1 s | -
|  | A |  | G01NHX01QN001-QM11 (QM03) | XB02 | - | 0 | - | BOOL | - | 1 s | - | and
|  | A |  | G01NHX01QN001-QM21 (QM05) | XB02 | - | 0 | - | BOOL | - | 1 s | -
Check and OK by AS 27042026 | How to check | A | 3.3 | G01NHX01KF201/KZ57 | XB01 | - | 1 | - | BOOL | - | 6 s | - | and | 1oo1 | N2 To H2 Side During Operation | 1=N2 To H2 Side | [5 empty] | S | S | S | S | [6 empty] | S | S | [26 empty] | indicate cause via message of Shut-Off Valve QM21 | 29.04.2025 implemented change | F. Reinhart | V3.1, 2024-01-26 (BM,FR): added new cause to cover loss of instrument air and fault of N2 control, which would lead to continious blow off of H2 to atmosphere. In this case the rectifier shall be shut down. V3.1, 2024-03-04 (BM+FR): "G01NHY01KF101-KZ11" changed to "G01NHY01KF101/KZ12;XB01" and "N2 To H2 Side" changed to "G01NHX01KF201/KZ57;XB01" V3.3, 2025-04-29 (FR): changed comment, indicate cause via message of Shut-Off Valve
|  | A |  | G01NHY01KF101/KZ12 | XB01 | - | 1 | - | BOOL | [6 empty] | 1=Array in operation | [15 empty] | S | S
Check and OK by AS 27042027 (Btank is Customer Scope) | How to check | A | 3.3 | G01NHX01KF201/KZ57 | XB01 | - | 1 | - | BOOL | - | 6 s | - | and | 1oo1 | N2 purging of product gas line | 1=N2 To H2 Side | [23 empty] | S | [19 empty] | if product valve closed too slow after impurity -> indicate cause via message of product valve | 29.04.2025 implemented change | F. Reinhart | V3.1, 2024-03-04 (FR): "N2 To H2 Side" changed to "G01NHX01KF201/KZ57;XB01" V3.3, 2025-02-29 (FR): Changed comment, indication of cause via message of product valve
|  | A |  | G01NHC01GT001-QN01/VLV | XB02 | - | 0 | - | BOOL | - | - | - |  |  |  | 0= Product Valve Not Closed
Array System Control
| Ckd by SG Not found this tag |  | 3.3_200 | GnyNHY01KF101-KZ80 | XM01 | - | 1 | - | BOOL | - | - | - |  |  | SIS - Communication Fault | 1= Fault of Lifebit Monitoring | [17 empty] | S | [6 empty] | S | S | [17 empty] | On communication fault to SIS: Rectifier Safe Off, Demin Supply Shufoff and Safety N2 Purge is caused in SIS. Pressure hold with N2 and correct function of Gas Analytic is not possible. Therefore shut down Gas Analytic. Furthermore the mentioned SIF Effects, which are caused in the SIS, shall be considered as active (or bad signal state) in the BPCS logic to react accordingly.
| Ckd by SG Not found this tag | A | 3.3 | CPU Restart |  | 0 | 0 | - | BOOL | - | - | - |  | 1oo1 | Process Control System not available | no message for this cause | [5 empty] | S | S | S | S | [34 empty] | inertization status not known | 29.04.2025 implemented change | F. Reinhart | V3.1 (BM, KB): when inertisation is required, operation of polrect and rectifier is not possible (see "Array inert required =G01NHB01KF201;XA02"), therfore not necessary to switch here off again. V3.3, FR, 2025-04-08: removed opening of MV circuit breaker because this will happen anyway, added "no message for this cause"
| Ckd by SG Not found this tag | A | 1.4 | G01NHY01KF101/KZ100 |  | - | 0 | - | BOOL | - | - | - |  | 1oo1 | Array - H2 ready | Interlock the product valve as long as array is not purged with H2 | [16 empty] | N | [26 empty] | The array must be purged with H2 before the gas is released to the buffer tank. The status "H2 ready" is set when the sum of the produced H2 exceeds 5 times the plant volume. The status is reset whenever N2 or O2 comes into the separators (see according interlock conditions). | 28.04.2025 no change | F. Reinhart
| Ckd by SG Not found this tag | A | 3.1 | G01NHY01KF101/KZ103 |  | - | 0 | - | BOOL | - | - |  |  | 1oo1 | Array - inert required | Interlock of Rectifiers | [5 empty] | N | N | N | N | [6 empty] | N | N |  | N | [25 empty] | 28.04.2025 no change | F. Reinhart | V2.0 31.08.2023: (BM, FR): added to avoid start of rectifiers when status "inert required" is active V3.1. (BM, KB), 8.1.2024: H2 ready shall be put "off"
Transformer (Thyripol) Customer's scope To be deleted |  | A
|  | A | 1.4 | G01NHA01TA001-BU01 | XM02 | - | 0 | - | BOOL | - | - | - |  | 1oo1 | Buchholz Protection | [29 empty] | S | [14 empty] | tap changer should remain in position, when transformer tripped -> fault analysis; rectifier is already interlocked by failsafe trip | 28.04.2025 no change | F. Reinhart | V1.4 (FR+AD): added causes for tap changer forced trip to prevent position change of tap changer after cirtical transformer trip V3.1: (BM) copied "V2.1 (FR+AD): added cause"
|  | A | 1.4 | G01NHA01TA001-BU02 | XM01 | - | 0 | - | BOOL | - | - |  |  | 1oo1 | Tap changer Protective Relay | [29 empty] | S | [15 empty] | 28.04.2025 no change | F. Reinhart
|  | A | 1.4 | G01NHA01TA001-BP01 | XM02 | - | 0 | - | BOOL | - | - |  |  | 1oo1 | Transformer Oil Pressure High | [29 empty] | S | [15 empty] | 28.04.2025 no change | F. Reinhart
|  | A | 3.1 | G01NHA01TA001-BP02 | XM02 | - | 0 | - | BOOL | - | - |  |  | 1oo1 | Tap Changer Oil Pressure High | [29 empty] | S | [15 empty] | 28.04.2025 no change | F. Reinhart
|  | A | 1.4 | G01NHA01TA001-FC01 | XG01 | - | 0 | - | BOOL | - | - |  |  | 1oo1 | Overcurrent protection 1 & 2 | [29 empty] | S | [15 empty] | 28.04.2025 no change | F. Reinhart
|  | A | 1.4 | G01NHA01TA001-FC02 | XG01 | - | 0 | - | BOOL | - | - |  |  | 1oo1 | Overcurrent protection 3 & 4 | [29 empty] | S | [15 empty] | 28.04.2025 no change | F. Reinhart
|  | A | 1.4 | G01NHA01TA001-QA02 | XM01 | - | 0 | - | BOOL | - | - |  |  | 1oo1 | Tap changer incomplete switching | [29 empty] | S | [15 empty] | 28.04.2025 no change | F. Reinhart
|  | A | 3.3 | G01NHA01TA001-BF01 | XM01 | - | 0 | - | BOOL | 10 s | 15 min | - |  | 2oo2 | No Trafo Oil Circulation (low flow) while Rectifier System On | 0=No Trafo oil circulation | [5 empty] | S | S | S | S | [17 empty] | S | [16 empty] | Only optional When no oil circulation flow is detected, then the temperature measurement of the transformer is not reliable. This means the rectifier current must be stopped to unload the transformer. It is sufficient to stop the rectifier, the MV circuit breaker can remain closed. Additionally the oil pump is stopped for pump protection. | Change implemented 20.03.2025 | P.Kumar | V3.1 & V2.1, 22.02.24 (FR+KB+AD): added cause, because missing V3.1, 2024-03-04 (BM+FR): "G01NHY01KF101-KZ11" changed to "G01NHY01KF101/KZ12;XB01" V3.3, Nemanja, BM, 2024.12.11: "only optional added" V3.3, 2025-03-28 (FR): "G01NHY01KF101/KZ12" changed to "G01NHA01KF201/KZ11" (Rectifier System State On)
|  | A |  | G01NHA01KF201/KZ11 | XB01 | - | 1 | - | BOOL | - | - |  |  |  |  | 1=Rectifier System State On
|  | A | 3.3 | G01NHA01TA001-BT01 | XQ01 | AH 105.0 | ASHH 120.0 | 2.0 | °C | - | - | - |  | 1oo1 | Oil Temperature High | [6 empty] | S | S | S | S | [34 empty] | project specific | Change implemented 20.03.2025 | P.Kumar | V3.3, FR, 16.01.2025: changed limit from 135/140 to 105/120 after feedback from Josef Niedernhuber
|  | A | 3.3 | G01NHA01TA001-BT02 | XQ01 | AH 125.0 | ASHH 140.0 | 2.0 | °C | - | - | - |  | 1oo1 | Winding Temperature High | [6 empty] | S | S | S | S | [34 empty] | project specific | Change implemented 20.03.2025 | P.Kumar | V3.3, FR, 16.01.2025: changed limit from 115/120 to 125/140 after feedback from Josef Niedernhuber
|  | A | 1.3 | G01NHA01TA001-FC01 | XJ01 | - | 0 | - | BOOL | - | - | - |  | 1oo1 | Overcurrent protection life bit | [6 empty] | S | S | S | S | [18 empty] | S | [15 empty] | Array shut down if life bit to protection relay is lost. After array shut down the MV circuit breaker shall be opened (to be confirmed project specifically) | 28.04.2025 no change | F. Reinhart | V2.0: 2023-08-31: (JS, RW, FH, BM): not connectet to SIS logic, since SIS logic triggers over current signal anyway when it is lost (signal "0")
|  | A |  |  | XJ02 | [16 empty] | S | S | S | S | [18 empty] | S
|  | A | 1.3 | G01NHA01TA001-FC02 | XJ01 | - | 0 | - | BOOL | - | - | - |  | 1oo1 | Overcurrent protection life bit | [6 empty] | S | S | S | S | [18 empty] | S | [16 empty] | 28.04.2025 no change | F. Reinhart
|  | A |  |  | XJ02 | [16 empty] | S | S | S | S | [18 empty] | S
MV supply (Customer's scope)
Customer Scope | Ckd by SG Connection not found with effect | A | 1.3 | T01BBA01QA00x-QA01 | XB01 | 0 | 0 | - | BOOL | - | - | - |  | 1oo1 | MV Circuit Breaker Open | not closed |  | S | S | S | S | [10 empty] | S | S | [26 empty] | not used for IGBT | 29.04.2025 no change | F. Reinhart
Discharge Resistor (Scope to be clarified)
|  | A | 3.3 | G01NHA01RA001-KF01 | XB13 | - | 1 | - | BOOL | - | - | - |  | 1oo1 | Discharge Resistor active | Check command | [5 empty] | N | N | N | N | [34 empty] | Interlock only enabled, when according row is enabled. | Change implemented 26.03.2025 | P.Kumar | V1.4 (FR): interlock only (pol.) rectifier of same row V2.1 (FR: added N1 for other rectifier rows V3.3, FR, 25.03.2025: Interlock of all Rectifier Rows, but only, when according row is enabled.
|  | A | 3.3 | G01NHA01RA002-KF01 | XB13 | - | 1 | - | BOOL | - | - | - |  | 1oo1 | Discharge Resistor active | Check command | [5 empty] | N | N | N | N | [34 empty] | Interlock only enabled, when according row is enabled. | Change implemented 26.03.2025 | P.Kumar
|  | A | 3.3 | G01NHA01RA003-KF01 | XB13 | - | 1 | - | BOOL | - | - | - |  | 1oo1 | Discharge Resistor active | Check command | [5 empty] | N | N | N | N | [34 empty] | Interlock only enabled, when according row is enabled. | Change implemented 26.03.2025 | P.Kumar
|  | A | 3.3 | G01NHA01RA004-KF01 | XB13 | - | 1 | - | BOOL | - | - | - |  | 1oo1 | Discharge Resistor active | Check command | [5 empty] | N | N | N | N | [34 empty] | Interlock only enabled, when according row is enabled. | Change implemented 26.03.2025 | P.Kumar
Rectifier Customer's scope
|  | A | 3.3 | G01NHA01TB001-KZ52 | XU01 | - | 1 | - | BOOL | - | - | - |  | 1oo1 | Rectif. 1 fault active | communicated via Rectifier |  | S | S | S | S | [10 empty] | S | S | [26 empty] | internal faults causing a common fault signal; Alarm only enabled, when according row is enabled. | 29.04.2025 implemented change | F. Reinhart | V1.4 (FR): specified common fault signal V3.3, BM, FR, 2024-11-14: changed from ramped to immediate shutdown. internal fault will suddely shut down the rectifier, so others should do the same. V3.3, FR, 25.03.2025: alarm/warning only enabled, when according row is enabled (removed S1/S2)
|  | A | 3.3 | G01NHA01TB002-KZ52 | XU01 | - | 1 | - | BOOL | - | - | - |  | 1oo1 | Rectif. 2 fault active | communicated via Rectifier |  | S | S | S | S | [10 empty] | S | S | [27 empty] | 29.04.2025 implemented change | F. Reinhart
|  | A | 3.3 | G01NHA01TB003-KZ52 | XU01 | - | 1 | - | BOOL | - | - | - |  | 1oo1 | Rectif. 3 fault active | communicated via Rectifier |  | S | S | S | S | [10 empty] | S | S | [27 empty] | 29.04.2025 implemented change | F. Reinhart
|  | A | 3.3 | G01NHA01TB004-KZ52 | XU01 | - | 1 | - | BOOL | - | - | - |  | 1oo1 | Rectif. 4 fault active | communicated via Rectifier |  | S | S | S | S | [10 empty] | S | S | [27 empty] | 29.04.2025 implemented change | F. Reinhart
|  | A | 3.3 | G01NHA01TB001-KZ56 | XM01 | - | 1 | - | BOOL | - | - | - |  | 1oo1 | Rectif. 1 communication fault | Lifebit evaluation |  | S | S | S | S | [10 empty] | S | S | [26 empty] | on communication fault the affected rectifer must stop itself (configured in rectifier); the rectifier is though interlocked to trigger the rectifier sequence and monitor the shutdown (in case of fault the sequence will trigger a shutdown via the failsafe commands); Alarm only enabled, when according row is enabled. | 29.04.2025 implemented change | F. Reinhart | V1.4 (FR+AD): added interlock for communication fault V3.3, BM, FR, 2024-11-14: changed from ramped to immediate shutdown. internal fault will suddely shut down the rectifier, so others should do the same. V3.3, FR, 25.03.2025: alarm/warning only enabled, when according row is enabled (removed S1/S2)
|  | A | 3.3 | G01NHA01TB002-KZ56 | XM01 | - | 1 | - | BOOL | - | - | - |  | 1oo1 | Rectif. 2 communication fault | Lifebit evaluation |  | S | S | S | S | [10 empty] | S | S | [27 empty] | 29.04.2025 implemented change | F. Reinhart
|  | A | 3.3 | G01NHA01TB003-KZ56 | XM01 | - | 1 | - | BOOL | - | - | - |  | 1oo1 | Rectif. 3 communication fault | Lifebit evaluation |  | S | S | S | S | [10 empty] | S | S | [27 empty] | 29.04.2025 implemented change | F. Reinhart
|  | A | 3.3 | G01NHA01TB004-KZ56 | XM01 | - | 1 | - | BOOL | - | - | - |  | 1oo1 | Rectif. 4 communication fault | Lifebit evaluation |  | S | S | S | S | [10 empty] | S | S | [27 empty] | 29.04.2025 implemented change | F. Reinhart
|  | A | 3.3 | G01NHA01TB001-KZ96 | XQ01 | - | = 60010 | - | BOOL | - | - | - |  | 1oo1 | Rectif. 1 Fault Code = 60010 | Uneven Current Distribution | [27 empty] | S | [15 empty] | On a thyristor fault of the rectifiers, the fuse for the according phase is tripped and the rectifier alarms this condition with fault code =60010 (Uneven Current Distribution). In this case the AC side is interconnected with the DC side of the Rectifier and the MV Circuit Breaker must be opened to protect a damage of the Rectifier Cooling equipment due to isolation issues. A shutdown of the rectifiers is already issued by "Fault Active" signal. | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB, 2025-04-08: added new cause
|  | A | 3.3 | G01NHA01TB002-KZ96 | XQ01 | - | = 60010 | - | BOOL | - | - | - |  | 1oo1 | Rectif. 2 Fault Code = 60010 | Uneven Current Distribution | [27 empty] | S | [16 empty] | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB, 2025-04-08: added new cause
|  | A | 3.3 | G01NHA01TB003-KZ96 | XQ01 | - | = 60010 | - | BOOL | - | - | - |  | 1oo1 | Rectif. 3 Fault Code = 60010 | Uneven Current Distribution | [27 empty] | S | [16 empty] | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB, 2025-04-08: added new cause
|  | A | 3.3 | G01NHA01TB004-KZ96 | XQ01 | - | = 60010 | - | BOOL | - | - | - |  | 1oo1 | Rectif. 4 Fault Code = 60010 | Uneven Current Distribution | [27 empty] | S | [16 empty] | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB, 2025-04-08: added new cause
|  | A | 3.3_201 | G01NHA01FA001-QA01 | XM01 | - | 0 | - | BOOL | - | - | - | and | 1oo1 | Overvoltage Protection - Rectifier 1 | 0= Overvolt. Prot. fault | [5 empty] | S | S | S | S | [6 empty] | S | S | [26 empty] | When overvoltage protection is faulty, array must not be started again. However it will not be tripped during operation. Alarm only enabled, when according row is enabled. | 29.04.2025 implemented change | F. Reinhart | V3.1 (FR+AD): added interlock V3.3, FR, 25.03.2025: alarm/warning only enabled, when according row is enabled (removed S1/S2)
|  | A |  | G01NHA01KF301/KZ11 | XB01 | - | 0 | - | BOOL | - | - | - |  |  |  | 0= Pulses not enabled
|  | A | 3.3_201 | G01NHA01FA002-QA01 | XM01 | - | 0 | - | BOOL | - | - | - | and | 1oo1 | Overvoltage Protection - Rectifier 2 | 0= Overvolt. Prot. fault | [5 empty] | S | S | S | S | [6 empty] | S | S | [26 empty] | When overvoltage protection is faulty, array must not be started again. However it will not be tripped during operation. Alarm only enabled, when according row is enabled. | 29.04.2025 implemented change | F. Reinhart | V3.1 (FR+AD): added interlock V3.3, FR, 25.03.2025: alarm/warning only enabled, when according row is enabled (removed S1/S2)
|  | A |  | G01NHA01KF302/KZ11 | XB01 | - | 0 | - | BOOL | - | - | - |  |  |  | 0= Pulses not enabled
|  | A | 3.3_201 | G01NHA01FA003-QA01 | XM01 | - | 0 | - | BOOL | - | - | - | and | 1oo1 | Overvoltage Protection - Rectifier 3 | 0= Overvolt. Prot. fault | [5 empty] | S | S | S | S | [6 empty] | S | S | [26 empty] | When overvoltage protection is faulty, array must not be started again. However it will not be tripped during operation. Alarm only enabled, when according row is enabled. | 29.04.2025 implemented change | F. Reinhart | V3.1 (FR+AD): added interlock V3.3, FR, 25.03.2025: alarm/warning only enabled, when according row is enabled (removed S1/S2)
|  | A |  | G01NHA01KF303/KZ11 | XB01 | - | 0 | - | BOOL | - | - | - |  |  |  | 0= Pulses not enabled
|  | A | 3.3_201 | G01NHA01FA004-QA01 | XM01 | - | 0 | - | BOOL | - | - | - | and | 1oo1 | Overvoltage Protection - Rectifier 4 | 0= Overvolt. Prot. fault | [5 empty] | S | S | S | S | [6 empty] | S | S | [26 empty] | When overvoltage protection is faulty, array must not be started again. However it will not be tripped during operation. Alarm only enabled, when according row is enabled. | 29.04.2025 implemented change | F. Reinhart | V3.1 (FR+AD): added interlock V3.3, FR, 25.03.2025: alarm/warning only enabled, when according row is enabled (removed S1/S2)
|  | A |  | G01NHA01KF304/KZ11 | XB01 | - | 0 | - | BOOL | - | - | - |  |  |  | 0= Pulses not enabled
Not to be considered in signal exchange list |  | A | 3.2 | G01NHA01EQ001-BP01 | XQ01 | AL 0.3 | ASLL 0.1 | 0.2 | bar(g) | - | 5 s | - |  | 1oo1 | Low Pressure Rect. Cooling Water | Set to 0 A DC instant |  | S | S | S | S | [15 empty] | S | [22 empty] | Interlock of Main Rectifier and cooling Pump can be deleted project specifically. Consequence: increase pump protection but lower availabilty (sensor Fault): to be discussed with customer | 29.04.2025 test required due to restructured Rectifier System | F. Reinhart | V1.4 changed from 1,0 bar warn to 0,3 bar. Changed 0,5 bar switch to 0,1 bar. V1.4 (FR): faster shutoff required V1.4 (BM): addtional Pumps switch off and remark revised V3.2, BM, 2024-07-02: "For Thyripol Rectifier only" added
Not to be considered in signal exchange list |  | A | 3.2 | G01NHA01EQ001-BP02 | XQ01 | AH 5.0 | ASHH 5.5 | 0.2 | bar(g) | - | 10 s | - |  | 1oo1 | High Pressure Rect. Cooling Water | Set to 0 A DC instant |  | S | S | S | S | [15 empty] | S | [22 empty] | Interlock of Main Rectifier and cooling Pump can be deleted project specifically. Consequence; avoidance of unintended release of deionat via saftey relief valve; but lower availabilty (sensor Fault): to be discussed with customer if deionat can be release into room of rectifiere cooling unit. | 29.04.2025 test required due to restructured Rectifier System | F. Reinhart | V1.4 (FR): faster shutoff required V1.4 (BM): addtional Pumps switch off and remark revised V3.0: (BM), 24.10.2023: Warning/alarm increased from 4/4.5 to 5/5.5 due to increased design pressure (old: 6 barg/new 8 barg) V3.2, BM, 2024-07-02: "For Thyripol Rectifier only" added
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01EQ001-BT01 | XQ01 | AL 3.0 | ASLL 2.0 | 1.0 | °C | - | - | - |  | 1oo1 | Freeze Protection Rectifier Cooling | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 test required due to restructured Rectifier System | F. Reinhart | V3.0, BM, 07.11.2023: Comment changed: new: time delay, trip by temp. Below dew point. V3.3, BM, 2025-05-13: Comment deleted since a control valve is considered anyway in V3.3
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB001-BF01 | XQ01 | AL 4.2 | ASLL 4.0 | 0.2 | m³/h | 5 s | 5 s | - |  | 2oo2 | Low Cooling Flow Rectifier 1 | normal flow 5 m³/h Signal communicated via rectifier |  | S | S | S | S | [38 empty] | Trip for DCM control is covered by Array control. Flow alarm low limit only enabled, when corresponding rectifier is in operation (impulse release) or Rectifier Cooling is in State On. Alarm only enabled, when according row is enabled. | 29.04.2025 implemented change | F. Reinhart | V1.4 (FR): faster shutoff required to protect rectifier V3.0: Thyripol: Trip is performed by internal Thyripol control. for Thyripol the sensor signal from -BF01 is communicated via the rectifier as -KZ85 V3.0, BM, 24.10.2023: values increased based on new modular rectifier design V3.2, 2024.06.12, BM: normal flow of 4 changed to 5 m³/h V3.2, BM, 2024-07-02: "For Thyripol Rectifier only" added V3.3, FR+KB, 2025-03-20: Added "NHA01KF305/KZ11" (Rectifier Cooling - State On) in order to monitor Cooling Flow already when Rectifier Cooling is started V3.3, FR, 25.03.2025: alarm/warning only enabled, when according row is enabled (removed S1/S2), removed "-KZ85" and use only sensor tag in software, added warning delay of 5s to suppress warning during pump start
Not to be considered in signal exchange list |  | A |  | G01NHA01TB001-KZ51 | XB01 | - | 1 | - | BOOL | - | - | - | or
Not to be considered in signal exchange list |  | A |  | G01NHA01KF305/KZ11 | XB01 | - | 1 | - | BOOL | - | - | -
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB002-BF01 | XQ01 | AL 4.2 | ASLL 4.0 | 0.2 | m³/h | 5 s | 5 s | - |  | 2oo2 | Low Cooling Flow Rectifier 2 |  |  | S | S | S | S | [39 empty] | 29.04.2025 implemented change | F. Reinhart
Not to be considered in signal exchange list |  | A |  | G01NHA01TB002-KZ51 | XB01 | - | 1 | - | BOOL | - | - | - | or
Not to be considered in signal exchange list |  | A |  | G01NHA01KF305/KZ11 | XB01 | - | 1 | - | BOOL | - | - | -
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB003-BF01 | XQ01 | AL 4.2 | ASLL 4.0 | 0.2 | m³/h | 5 s | 5 s | - |  | 2oo2 | Low Cooling Flow Rectifier 3 |  |  | S | S | S | S | [39 empty] | 29.04.2025 implemented change | F. Reinhart
Not to be considered in signal exchange list |  | A |  | G01NHA01TB003-KZ51 | XB01 | - | 1 | - | BOOL | - | - | - | or
Not to be considered in signal exchange list |  | A |  | G01NHA01KF305/KZ11 | XB01 | - | 1 | - | BOOL | - | - | -
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB004-BF01 | XQ01 | AL 4.2 | ASLL 4.0 | 0.2 | m³/h | 5 s | 5 s | - |  | 2oo2 | Low Cooling Flow Rectifier 4 |  |  | S | S | S | S | [39 empty] | 29.04.2025 implemented change | F. Reinhart
Not to be considered in signal exchange list |  | A |  | G01NHA01TB004-KZ51 | XB01 | - | 1 | - | BOOL | - | - | - | or
Not to be considered in signal exchange list |  | A |  | G01NHA01KF305/KZ11 | XB01 | - | 1 | - | BOOL | - | - | -
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01EQ001-KZ31 |  | AL 18.0 | ASLL 16.0 | 1.0 | m³/h | 5 s | 5 s | - |  | 1oo1 | Low Total Flow Rectifier Cooling | sum of all 4 rectifier flows (KZ31) low | [20 empty] | S | [22 empty] | Pump protection only enabled when pump is running. | 29.04.2025 implemented change | F. Reinhart | V1.4 (FR): faster shutoff required V1.4 (BM): delete pump switch over in case of low flow alarm V3.0, BM, 24.10.2023: new value; pump protection; no protection of rectifiers (makes only sense when only two rectifiers operate, than 2*4m³/h + 2 m³/h) V3.2, BM, 2024-07-02: "For Thyripol Rectifier only" added V3.3, FR, 2025-02-18: added W_DC of 5s to prevent message on pump start
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB001-BT01 | XQ01 | AH 85.0 | ASHH 90.0 | 1.0 | °C | - | 1 s | - |  | 1oo1 | High Busbar Temp. Phase U - Rectifier 1 | Signal communicated via rectifier | [5 empty] | S | S | S | S | [34 empty] | Alarm only enabled, when according row is enabled. | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB, 2025-04-08: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB001-BT02 | XQ01 | AH 85.0 | ASHH 90.0 | 1.0 | °C | - | 1 s | - |  | 1oo1 | High Busbar Temp. Phase V - Rectifier 1 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB, 2025-04-08: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB001-BT03 | XQ01 | AH 85.0 | ASHH 90.0 | 1.0 | °C | - | 1 s | - |  | 1oo1 | High Busbar Temp. Phase W - Rectifier 1 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB, 2025-04-08: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB002-BT01 | XQ01 | AH 85.0 | ASHH 90.0 | 1.0 | °C | - | 1 s | - |  | 1oo1 | High Busbar Temp. Phase U - Rectifier 2 | Signal communicated via rectifier | [5 empty] | S | S | S | S | [34 empty] | Alarm only enabled, when according row is enabled. | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB, 2025-04-08: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB002-BT02 | XQ01 | AH 85.0 | ASHH 90.0 | 1.0 | °C | - | 1 s | - |  | 1oo1 | High Busbar Temp. Phase V - Rectifier 2 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB, 2025-04-08: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB002-BT03 | XQ01 | AH 85.0 | ASHH 90.0 | 1.0 | °C | - | 1 s | - |  | 1oo1 | High Busbar Temp. Phase W - Rectifier 2 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB, 2025-04-08: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB003-BT01 | XQ01 | AH 85.0 | ASHH 90.0 | 1.0 | °C | - | 1 s | - |  | 1oo1 | High Busbar Temp. Phase U - Rectifier 3 | Signal communicated via rectifier | [5 empty] | S | S | S | S | [34 empty] | Alarm only enabled, when according row is enabled. | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB, 2025-04-08: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB003-BT02 | XQ01 | AH 85.0 | ASHH 90.0 | 1.0 | °C | - | 1 s | - |  | 1oo1 | High Busbar Temp. Phase V - Rectifier 3 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB, 2025-04-08: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB003-BT03 | XQ01 | AH 85.0 | ASHH 90.0 | 1.0 | °C | - | 1 s | - |  | 1oo1 | High Busbar Temp. Phase W - Rectifier 3 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB, 2025-04-08: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB004-BT01 | XQ01 | AH 85.0 | ASHH 90.0 | 1.0 | °C | - | 1 s | - |  | 1oo1 | High Busbar Temp. Phase U - Rectifier 4 | Signal communicated via rectifier | [5 empty] | S | S | S | S | [34 empty] | Alarm only enabled, when according row is enabled. | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB, 2025-04-08: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB004-BT02 | XQ01 | AH 85.0 | ASHH 90.0 | 1.0 | °C | - | 1 s | - |  | 1oo1 | High Busbar Temp. Phase V - Rectifier 4 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB, 2025-04-08: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB004-BT03 | XQ01 | AH 85.0 | ASHH 90.0 | 1.0 | °C | - | 1 s | - |  | 1oo1 | High Busbar Temp. Phase W - Rectifier 4 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB, 2025-04-08: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB001-BT01 | XQ01 | AL 3.0 | ASLL 2.0 | 1.0 | °C | - | 10 s | - |  | 1oo1 | Low Busbar Temp. Phase U - Rectifier 1 | Low trip is required to react on sensor fault. Signal communicated via rectifier | [5 empty] | S | S | S | S | [34 empty] | Alarm only enabled, when according row is enabled. On low temperature, it must be checked that the cooling dose at the rectifier busbar did not take any damage due to freezing. Low temperature may also be indicated on sensor fault. | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB+UG, 2025-04-29: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB001-BT02 | XQ01 | AL 3.0 | ASLL 2.0 | 1.0 | °C | - | 10 s | - |  | 1oo1 | Low Busbar Temp. Phase V - Rectifier 1 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB+UG, 2025-04-29: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB001-BT03 | XQ01 | AL 3.0 | ASLL 2.0 | 1.0 | °C | - | 10 s | - |  | 1oo1 | Low Busbar Temp. Phase W - Rectifier 1 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB+UG, 2025-04-29: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB002-BT01 | XQ01 | AL 3.0 | ASLL 2.0 | 1.0 | °C | - | 10 s | - |  | 1oo1 | Low Busbar Temp. Phase U - Rectifier 2 | Low trip is required to react on sensor fault. Signal communicated via rectifier | [5 empty] | S | S | S | S | [34 empty] | Alarm only enabled, when according row is enabled. On low temperature, it must be checked that the cooling dose at the rectifier busbar did not take any damage due to freezing. Low temperature may also be indicated on sensor fault. | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB+UG, 2025-04-29: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB002-BT02 | XQ01 | AL 3.0 | ASLL 2.0 | 1.0 | °C | - | 10 s | - |  | 1oo1 | Low Busbar Temp. Phase V - Rectifier 2 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB+UG, 2025-04-29: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB002-BT03 | XQ01 | AL 3.0 | ASLL 2.0 | 1.0 | °C | - | 10 s | - |  | 1oo1 | Low Busbar Temp. Phase W - Rectifier 2 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB+UG, 2025-04-29: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB003-BT01 | XQ01 | AL 3.0 | ASLL 2.0 | 1.0 | °C | - | 10 s | - |  | 1oo1 | Low Busbar Temp. Phase U - Rectifier 3 | Low trip is required to react on sensor fault. Signal communicated via rectifier | [5 empty] | S | S | S | S | [34 empty] | Alarm only enabled, when according row is enabled. On low temperature, it must be checked that the cooling dose at the rectifier busbar did not take any damage due to freezing. Low temperature may also be indicated on sensor fault. | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB+UG, 2025-04-29: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB003-BT02 | XQ01 | AL 3.0 | ASLL 2.0 | 1.0 | °C | - | 10 s | - |  | 1oo1 | Low Busbar Temp. Phase V - Rectifier 3 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB+UG, 2025-04-29: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB003-BT03 | XQ01 | AL 3.0 | ASLL 2.0 | 1.0 | °C | - | 10 s | - |  | 1oo1 | Low Busbar Temp. Phase W - Rectifier 3 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB+UG, 2025-04-29: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB004-BT01 | XQ01 | AL 3.0 | ASLL 2.0 | 1.0 | °C | - | 10 s | - |  | 1oo1 | Low Busbar Temp. Phase U - Rectifier 4 | Low trip is required to react on sensor fault. Signal communicated via rectifier | [5 empty] | S | S | S | S | [34 empty] | Alarm only enabled, when according row is enabled. On low temperature, it must be checked that the cooling dose at the rectifier busbar did not take any damage due to freezing. Low temperature may also be indicated on sensor fault. | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB+UG, 2025-04-29: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB004-BT02 | XQ01 | AL 3.0 | ASLL 2.0 | 1.0 | °C | - | 10 s | - |  | 1oo1 | Low Busbar Temp. Phase V - Rectifier 4 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB+UG, 2025-04-29: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB004-BT03 | XQ01 | AL 3.0 | ASLL 2.0 | 1.0 | °C | - | 10 s | - |  | 1oo1 | Low Busbar Temp. Phase W - Rectifier 4 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart | V3.3, FR+MB+UG, 2025-04-29: added new cause
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB001-BF01 | XQ02 | AH 54.5 | ASHH 56.0 | 1.0 | °C | - | 1 s | - |  | 1oo1 | High Cooling Temp. Rectifier 1 | Max. normal return temp. ~51°C. Signal communicated via rectifier | [5 empty] | S | S | S | S | [34 empty] | Alarm only enabled, when according row is enabled. | 29.04.2025 implemented change | F. Reinhart | V3.0, BM, 24.10.2023: new rectifier design, temperature sensor changed to return line and values adopted. V3.2, BM, 2024-07-02: "For Thyripol Rectifier only" added V3.3, FR, 25.03.2025: alarm/warning only enabled, when according row is enabled (removed S1/S2), removed "-KZ86" and use only sensor tag in software
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB002-BF01 | XQ02 | AH 54.5 | ASHH 56.0 | 1.0 | °C | - | 1 s | - |  | 1oo1 | High Cooling Temp. Rectifier 2 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB003-BF01 | XQ02 | AH 54.5 | ASHH 56.0 | 1.0 | °C | - | 1 s | - |  | 1oo1 | High Cooling Temp. Rectifier 3 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB004-BF01 | XQ02 | AH 54.5 | ASHH 56.0 | 1.0 | °C | - | 1 s | - |  | 1oo1 | High Cooling Temp. Rectifier 4 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB001-BF01 | XQ02 | AL 10.0 | ASLL 5.0 | 1.0 | °C | - | 10 s | - |  | 1oo1 | Low Cooling Temp. Rectifier 1 | Low trip is required to react on sensor fault. Signal communicated via rectifier | [5 empty] | S | S | S | S | [34 empty] | Alarm only enabled, when according row is enabled. | 29.04.2025 implemented change | F. Reinhart | V3.3, FR, 27.09.2024: added trip on low temperature to react on sensor fault (this is now neccessary, because the signal is communicated as 0 or negative value by rectifier without signal state, rectifier does not trip itself) V3.3, FR, 25.03.2025: alarm/warning only enabled, when according row is enabled (removed S1/S2), removed "-KZ86" and use only sensor tag in software
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB002-BF01 | XQ02 | AL 10.0 | ASLL 5.0 | 1.0 | °C | - | 10 s | - |  | 1oo1 | Low Cooling Temp. Rectifier 2 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB003-BF01 | XQ02 | AL 10.0 | ASLL 5.0 | 1.0 | °C | - | 10 s | - |  | 1oo1 | Low Cooling Temp. Rectifier 3 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB004-BF01 | XQ02 | AL 10.0 | ASLL 5.0 | 1.0 | °C | - | 10 s | - |  | 1oo1 | Low Cooling Temp. Rectifier 4 | [6 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart
Not to be considered in signal exchange list |  | A | 3.2 | G01NHA01EQ001-BQ01 | XQ01 | AH 1.0 | ASHH 2.5 | 0.2 | µS/cm | - | 30 s | - |  | 1oo1 | Conductivity Monitoring Rectifier | [6 empty] | S | S | S | S | [34 empty] | A trip of rectifier at high conductivity is not mandatory in terms of personnel protection (potential carry over to rectifier cooling is not relevant & rectifier room is not accessible during operation). Only a damage of rectifier (short circuit) is expected at very high conductivities (worst case). Thus, only a warning is mandatory. Nevertheless, a trip can be implemented project specifically to avoid technical damage on the rectifier (short circuit). | 29.04.2025 test required due to restructured Rectifier System | F. Reinhart | V1.4 (FR): project specific interlocks should be considered in the reference software by default -> if not required, they can be removed in the project V3.0, BM, 25.10.2023: changed from 10/25 µS/cm to 1/2,5. see mail from Ulf Geck (25.10.2023). Lower conductivity for modular rectifier necessary to get sufficient electrical isolation. V3.2, BM, 2024-07-02: "For Thyripol Rectifier only" added
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01BZ011-TF01 | XW02 |  | 0 |  | BOOL | - |  |  |  | 1oo1 | Isolation Alarm - Rectifier 1 | Fault of isolation measurement | [5 empty] | S | S | S | S | [34 empty] | Alarm only enabled, when according row is enabled. | 29.04.2025 implemented change | F. Reinhart | V1.4 (FR): on fault of isolation measurement, the analog value can not be trusted and the (pol.) rectifier must be shutoff V3.3, FR, 25.03.2025: alarm/warning only enabled, when according row is enabled (removed S1/S2)
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01BZ012-TF01 | XW02 |  | 0 |  | BOOL | - |  |  |  | 1oo1 | Isolation Alarm - Rectifier 2 | Fault of isolation measurement | [5 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01BZ013-TF01 | XW02 |  | 0 |  | BOOL | - |  |  |  | 1oo1 | Isolation Alarm - Rectifier 3 | Fault of isolation measurement | [5 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01BZ014-TF01 | XW02 |  | 0 |  | BOOL | - |  |  |  | 1oo1 | Isolation Alarm - Rectifier 4 | Fault of isolation measurement | [5 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01BZ011-TF01 | XQ01 | AL 100.0 | ASLL 40.0 | 10.0 | kOhm | - | 10 s | - |  | 1oo1 | Isolation monitoring | Analog process signal | [5 empty] | S | S | S | S | [6 empty] | S | S | [26 empty] | - project specific, adjust during commissioning Alarm only enabled, when according row is enabled. | 29.04.2025 implemented change | F. Reinhart | V1.4 (FR): on fault of isolation measurement, the analog value can not be trusted and the (pol.) rectifier must be shutoff V3.3, FR, 25.03.2025: alarm/warning only enabled, when according row is enabled (removed S1/S2) V3.3, MB, 13.05.2025: warning reduced from 150 to 100 kOhm
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01BZ012-TF01 | XQ01 | AL 100.0 | ASLL 40.0 | 10.0 | kOhm | - | 10 s | - |  | 1oo1 | Isolation monitoring | Analog process signal | [5 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 29.04.2025 implemented change | F. Reinhart
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01BZ013-TF01 | XQ01 | AL 100.0 | ASLL 40.0 | 10.0 | kOhm | - | 10 s | - |  | 1oo1 | Isolation monitoring | Analog process signal | [5 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 29.04.2025 implemented change | F. Reinhart
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01BZ014-TF01 | XQ01 | AL 100.0 | ASLL 40.0 | 10.0 | kOhm | - | 10 s | - |  | 1oo1 | Isolation monitoring | Analog process signal | [5 empty] | S | S | S | S | [6 empty] | S | S | [27 empty] | 29.04.2025 implemented change | F. Reinhart
Note: 1 Thes interlocks were considered for XXX were considered in SE scope (change order expected) |  | A | 3.3 | G01NHA01QZ001-QB01 | XB01 | - | 0 | - | BOOL | - | - | - |  | 1oo2 | DC+ or DC -disconnector Rectifier 1 - not open | [10 empty] | N | [33 empty] | Discharge resistor must not be activated, when DC+ or DC- disconnector is not open | 29.04.2025 implemented change | F. Reinhart | V1.4 added cause V3.0, BM, 07.11.2023: "circuit breaker" changed to disconnector and second disconnectors (DC-) added. V3.3, BM, FR, 20240930: "XB02" changed to "XB01"
|  | A |  | G01NHA01QZ001-QB02 | XB01 | - | 0 | - | BOOL | -
|  | A | 3.3 | G01NHA01QZ002-QB01 | XB01 | - | 0 | - | BOOL | - | - | - |  | 1oo2 | DC+ or DC -disconnector Rectifier 2 - not open | [11 empty] | N | [33 empty] | 29.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHA01QZ002-QB02 | XB01 | - | 0 | - | BOOL | -
|  | A | 3.3 | G01NHA01QZ003-QB01 | XB01 | - | 0 | - | BOOL | - | - | - |  | 1oo2 | DC+ or DC -disconnector Rectifier 3 - not open | [12 empty] | N | [32 empty] | 29.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHA01QZ003-QB02 | XB01 | - | 0 | - | BOOL | -
|  | A | 3.3 | G01NHA01QZ004-QB01 | XB01 | - | 0 | - | BOOL | - | - | - |  | 1oo2 | DC+ or DC -disconnector Rectifier 4 - not open | [13 empty] | N | [31 empty] | 29.04.2025 implemented change | F. Reinhart
|  | A |  | G01NHA01QZ004-QB02 | XB01 | - | 0 | - | BOOL | -
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB001-KZ51 | XB01 | - | 1 | - | BOOL | - | 40/66 s for AH/ASHH | - | and | 2oo2 | Rectifier 1 current control failure | 1= Pulses Enabled | [5 empty] | S | S | S | S | [34 empty] | Thyripol Control failure. Measured value of rectifier current differs to much from set point, while rectifier is in operation and not waiting for tap changer. Alarm only enabled, when according row is enabled. | 29.04.2025 implemented change | F. Reinhart | V2.0 added V3.0, BM, 25.10.2023: TAG no of SIS current measurment changed V3.3, FR, 25.03.2025: alarm/warning only enabled, when according row is enabled (removed S1/S2)
Not to be considered in signal exchange list |  | A |  | G01NHA01TB001-KZ54 | XH52 | - | 0 | - | BOOL | - | [5 empty] | 0= Alpha G Limit not reached
Not to be considered in signal exchange list |  | A |  | G01NHA01BZ011-KZ03 | XQ01 | AH ¦300.0¦ | ASHH ¦300.0¦ | 100.0 | A | - | [5 empty] | Delta between G01NHA01TB001-KZ21 and G01NHA01BZ001-BC02
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB002-KZ51 | XB01 | - | 1 | - | BOOL | - | 40/66 s for AH/ASHH | - | and | 2oo2 | Rectifier 2 current control failure | 1= Pulses Enabled | [5 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart
Not to be considered in signal exchange list |  | A |  | G01NHA01TB002-KZ54 | XH52 | - | 0 | - | BOOL | - | [5 empty] | 0= Alpha G Limit not reached
Not to be considered in signal exchange list |  | A |  | G01NHA01BZ012-KZ03 | XQ01 | AH ¦300.0¦ | ASHH ¦300.0¦ | 100.0 | A | - | [5 empty] | Delta between G01NHA01TB002-KZ21 and G01NHA01BZ002-BC02
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB003-KZ51 | XB01 | - | 1 | - | BOOL | - | 40/66 s for AH/ASHH | - | and | 2oo2 | Rectifier 3 current control failure | 1= Pulses Enabled | [5 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart
Not to be considered in signal exchange list |  | A |  | G01NHA01TB003-KZ54 | XH52 | - | 0 | - | BOOL | - | [5 empty] | 0= Alpha G Limit not reached
Not to be considered in signal exchange list |  | A |  | G01NHA01BZ013-KZ03 | XQ01 | AH ¦300.0¦ | ASHH ¦300.0¦ | 100.0 | A | - | [5 empty] | Delta between G01NHA01TB003-KZ21 and G01NHA01BZ003-BC02
Not to be considered in signal exchange list |  | A | 3.3 | G01NHA01TB004-KZ51 | XB01 | - | 1 | - | BOOL | - | 40/66 s for AH/ASHH | - | and | 2oo2 | Rectifier 4 current control failure | 1= Pulses Enabled | [5 empty] | S | S | S | S | [35 empty] | 29.04.2025 implemented change | F. Reinhart
Not to be considered in signal exchange list |  | A |  | G01NHA01TB004-KZ54 | XH52 | - | 0 | - | BOOL | - | [5 empty] | 0= Alpha G Limit not reached
Not to be considered in signal exchange list |  | A |  | G01NHA01BZ014-KZ03 | XQ01 | AH ¦300.0¦ | ASHH ¦300.0¦ | 100.0 | A | - | [5 empty] | Delta between G01NHA01TB004-KZ21 and G01NHA01BZ004-BC02
Note:
1 | There is no specific constant pressure piston buffer tank in H2 Sakura project downstream of product control valve. Hence customer's contant volume tank to be reffered as buffer tank/volume | There is no specific constant pressute piston buffer tank on H2 Yes prpject downstream of product control valve. Hence customer's scope piping volume to be reffered as buffer tank/volume
2 | The cause-and-effect relationships outlined herein are provided solely on the basis of Siemens Energy’s limited experience with complete plant configurations. They are intended for preliminary guidance only and shall not be construed as comprehensive, exhaustive, or finalized from Siemens Energy’s side. | The cause-and-effect relationships outlined herein are provided solely on the basis of Siemens Energy’s limited experience with complete plant configurations. They are intended for preliminary guidance only and shall not be construed as comprehensive, exhaustive, or finalized from Siemens Energy’s side.
| The Customer shall bear full responsibility for conducting detailed investigations, including but not limited to project-specific HAZOP and HAZID studies, to identify any critical causes at the complete plant level that may trigger array safety-related effects. | The Customer shall bear full responsibility for conducting detailed investigations, including but not limited to project-specific HAZOP and HAZID studies, to identify any critical causes at the complete plant level that may trigger array safety-related effects.
| Any additional causes or effects identified by the Customer may be proposed for inclusion. Incorporation into the safety matrix and associated logic shall be subject to mutual agreement between Siemens Energy and the Customer. | Any additional causes or effects identified by the Customer may be proposed for inclusion. Incorporation into the safety matrix and associated logic shall be subject to mutual agreement between Siemens Energy and the Customer.
Transformer (IGBT) - OPTIONAL
|  |  | 3.3 | G01NHA01TA001-BU01 | XM02 | - | 0 | - | BOOL | - | - | - |  | 1oo1 | Buchholz Protection | [6 empty] | S | S | [21 empty] | S | [14 empty] | tap changer should remain in position, when transformer tripped -> fault analysis; rectifier is already interlocked by failsafe trip When MV CB not closed, rectifier should be off already and interlocked for switching on -> only to detect faulty MV CB feedback
|  |  | 3.3 | G01NHA01TA001-BU02 | XM01 | - | 0 | - | BOOL | - | - | - |  | 1oo1 | Tap changer Protective Relay | [6 empty] | S | S | [21 empty] | S
|  |  | 3.3 | G01NHA01TA001-BP01 | XM02 | - | 0 | - | BOOL | - | - | - |  | 1oo1 | Transformer Oil Pressure High | [6 empty] | S | S | [21 empty] | S
|  |  | 3.3 | G01NHA01TA001-BT01 | XM01 | - | 0 | - | BOOL | - | - | - |  | 1oo1 | Oil Temp. Transformer Alarm | Operator to check setpoint | [42 empty] | S |  |  |  | new for IGBT
[6 empty] | - | 0 | - | BOOL | - | 10 min | - |  | 1oo1 | [7 empty] | S | S | [21 empty] | S
|  |  | 3.3 | G01NHA01TA001-BP02 | XM02 | - | 0 | - | BOOL | - | - | - |  | 1oo1 | Tap Changer Oil Pressure High | [29 empty] | S | [17 empty] | can be deleted since burst disc is sufficient
|  |  | 3.3 | G01NHA01TA001-QA02 | XM01 | - | 0 | - | BOOL | - | - | - |  | 1oo1 | Tap changer incomplete switching | [6 empty] | S | S | [21 empty] | S
|  |  | 3.3 | G01NHA01TA001-BT01 | XM01 | AH 135.0 | ASHH 140.0 | 2.0 | °C | - | - | - |  | 1oo1 | Oil Temperature High | [6 empty] | S | S1 | [39 empty] | not needed since switch for warning and trip is already considered.
|  |  | 3.3 | G01NHA01TA001-BT02 | XM01 | AH 115.0 | ASHH 120.0 | 2.0 | °C | - | - | - |  | 1oo1 | Winding Temperature High | [6 empty] | S | S | [39 empty] | removed since not a real measurment ("fake measurment") but only calculated based on winding currents
|  |  | 3.3 | T01BBA01QA00x-QA01 | XB01 | - | 0 | - | BOOL | - | - |  |  | 1oo1 | MV CB Row 1 not closed | [6 empty] | S | S
|  |  | 3.3 | G01NHA01TA002-BU01 | XM01 | - | 0 | - | BOOL | - | - | - |  | 1oo1 | Buchholz Protection | [6 empty] | S | S | [22 empty] | S | S
|  |  | 3.3 | G01NHA01TA002-BU02 | XM01 | - | 0 | - | BOOL | - | - | - |  | 1oo1 | Tap changer Protective Relay | [6 empty] | S | S | [22 empty] | S | S
|  |  | 3.3 | G01NHA01TA002-BP01 | XM02 | - | 0 | - | BOOL | - | - | - |  | 1oo1 | Transformer Oil Pressure High | [6 empty] | S | S | [22 empty] | S | S
|  |  | 3.3 | G01NHA01TA002-BT01 | XM01 | - | 0 | - | BOOL | - | - | - |  | 1oo1 | Oil Temp. Transformer Alarm | Operator to check setpoint | [42 empty] | S |  |  |  | new for IGBT
[6 empty] | - | 0 | - | BOOL | - | 10 min | - |  | 1oo1 | [7 empty] | S | S | [22 empty] | S | S
|  |  | 3.3 | G01NHA01TA002-BP02 | XM02 | - | 0 | - | BOOL | - | - | - |  | 1oo1 | Tap Changer Oil Pressure High | [30 empty] | S | S | [15 empty] | can be deleted since burst disc is sufficient
|  |  | 3.3 | G01NHA01TA002-QA02 | XM01 | - | 0 | - | BOOL | - | - | - |  | 1oo1 | Tap changer incomplete switching | [6 empty] | S | S | [22 empty] | S | S
|  |  | 3.3 | G01NHA01TA002-BT01 | XQ01 | AH 135.0 | ASHH 140.0 | 2.0 | °C | - | - | - |  | 1oo1 | Oil Temperature High | [6 empty] | S2 | S | [22 empty] | S | S | [15 empty] | not needed since switch for warning and trip is already considered.
|  |  | 3.3 | G01NHA01TA002-BT02 | XQ01 | AH 115.0 | ASHH 120.0 | 2.0 | °C | - | - | - |  | 1oo1 | Winding Temperature High | [6 empty] | S2 | S | [22 empty] | S | S | [15 empty] | removed since not a real measurment ("fake measurment") but only calculated based on winding currents
|  |  | 3.3 | T01BBA01QA00x-QA02 | XB01 | - | 0 | - | BOOL | - | - |  |  | 1oo1 | MV CB Row 2 not closed | [6 empty] | S | S
MV supply (IGBT) - OPTIONAL
|  |  | 3.3N | T01BBA01QA00x-BC01 | XM01 | - | 0 | - | BOOL | - | - |  |  | 1oo1 | Overcurrent protection row 1 | [29 empty] | S
|  |  | 3.3 | T01BBA01QA00x-QA01 | XB01 | 0 | 0 | - | BOOL | - | - | - |  | 1oo1 | MV Circuit Breaker Open | MV CB 1 not closed |  | S | S
|  |  | 3.3N | T01BBA01QA00x-BC02 | XM01 | - | 0 | - | BOOL | - | - |  |  | 1oo1 | Overcurrent protection row 2 | [30 empty] | S | S
|  |  | 3.3 | T01BBA01QA00x-QA02 | XB01 | 0 | 0 | - | BOOL | - | - | - |  | 1oo1 | MV Circuit Breaker Open | MV CB 2 not closed |  | S | S
Discharge Resistor (IGBT) - OPTIONAL
|  |  | 3.3 | G01NHA01RA001-KF01 | XB13 | - | 1 | - | BOOL | - | - | - |  | 1oo1 | Discharge Resistor active | Check command | [35 empty] | N | N |  |  | N |  |  |  | Signal is only accepted if the DC contactor is open. |  |  | V3.3, BM, 20240902:Kommentar ergänzt
|  |  | 3.3 | G01NHA01RA002-KF01 | XB13 | - | 1 | - | BOOL | - | - | - |  | 1oo1 | Discharge Resistor active | Check command | [37 empty] | N | N |  | N
Rectifier (IGBT) - OPTIONAL
|  |  | 3.3 | G01NHA01TB001-KZ52 | XU01 | - | 1 | - | BOOL | - | - | - |  | 1oo1 | Rectif. Row 1 fault active | communicated via Rectifier |  | S4) |  |  |  | S | S | [36 empty] | - Effected power line is switched off by converter controller instantaneously, after short communication delay parallel power line is switched off by converter controller instantaneously, too - Internal faults causing a common fault signal (including overvoltage, IGBT fault,...); - Trip all rectifiers because asynchronous operation is not allowed - Electrolyzer controller sends normal stop to both rectifier rows (both IC2 controllers).
|  |  | 3.3 | G01NHA01TB002-KZ52 | XU01 | - | 1 | - | BOOL | - | - | - |  | 1oo1 | Rectif. Row 2 fault active | communicated via Rectifier |  |  | S4) |  |  | S | S
|  |  | 3.3 | G01NHA01TB001-KZ56 | XM01 | - | 1 | - | BOOL | - | - | - |  | 1oo1 | Rectif. Row 1 communication fault | Lifebit evaluation | [5 empty] | S | S | [36 empty] | - When communication is lost effected IC2 controller initiates a current ramp down with 10 % / s to minimum operation current (e.g. 40 %); 30 s after minimum current has reached ACB is open - Trip all rectifiers because asynchronous operation is not allowed - Electrolyzer controller sends normal stop to both rectifier rows (both IC2 controllers).
|  |  | 3.3 | G01NHA01TB002-KZ56 | XM01 | - | 1 | - | BOOL | - | - | - |  | 1oo1 | Rectif. Row 2 communication fault | Lifebit evaluation | [5 empty] | S | S
|  |  | 3.3 | G01NHA01BZ011-TF01 | XW02 |  | 0 |  | BOOL | - |  |  |  | 1oo1 | Isolation Alarm - Rectifier Row 1 | Fault of isolation measurement | [5 empty] | S | S
|  |  | 3.3 | G01NHA01BZ012-TF01 | XW02 |  | 0 |  | BOOL | - |  |  |  | 1oo1 | Isolation Alarm - Rectifier Row 2 | Fault of isolation measurement | [5 empty] | S | S
|  |  | 3.3 | G01NHA01BZ011-TF01 | XQ01 | AL 150.0 | ASLL 40.0 | 10.0 | kOhm | - | 10 s | - |  | 1oo1 | Isolation monitoring Row 1 | Analog process signal | [5 empty] | S | S | [36 empty] | - project specific, adjust during commissioning
|  |  | 3.3 | G01NHA01BZ012-TF01 | XQ01 | AL 150.0 | ASLL 40.0 | 10.0 | kOhm | - | 10 s | - |  | 1oo1 | Isolation monitoring Row 2 | Analog process signal | [5 empty] | S | S
|  |  | 3.3 | G01NHA01QZ001-QA12 | XB02 | - | 0 | - | BOOL | - | - | - |  | 1oo4 | DC side Row 1 not disconneted | DC disconnector or DC precharge disconnector not open | [6 empty] | S |  |  | N | [25 empty] | N | N |  |  | S |  |  |  | - All contactors and breakers of the power unit (2 power lines / half a row) are open excluding the discharge resistor contactor. - Logic implemented by internal IGBT system. - To be checked by Ingeteam if discharge resistor activation is accepted. - Command to connect discharge resistor and feedback is exchanged via Profinet and directly displayed at electrolyzer operator system - Trip all rectifiers because asynchronous operation is not allowed - Electrolyzer controller sends normal stop to both rectifier rows (both IC2 controllers). |  |  | V3.3, BM, 20240902: DC pre charge rectifier 2 was missing
|  |  |  | G01NHA01QZ001-QA32 | XB02 | - | 0 | - | BOOL | - | - | -
|  |  |  | G01NHA01QZ001-QA13 | XB02 | - | 0 | - | BOOL | - | - | -
|  |  |  | G01NHA01QZ001-QA33 | XB02 | - | 0 | - | BOOL | - | - | -
|  |  | 3.3 | G01NHA01QZ002-QA12 | XB02 | - | 0 | - | BOOL | - | - | - |  | 1oo4 | DC side Row 2 not disconneted | [6 empty] | S |  |  |  |  | N | [26 empty] | N | N |  | S
|  |  |  | G01NHA01QZ002-QA32 | XB02 | - | 0 | - | BOOL | - | - | -
|  |  |  | G01NHA01QZ002-QA13 | XB02 | - | 0 | - | BOOL | - | - | -
|  |  |  | G01NHA01QZ002-QA33 | XB02 | - | 0 | - | BOOL | - | - | -
|  |  | 3.3 | G01NHA01QZ001-QA12 | GrpErr | - | 1 | - | BOOL | - | - | - | - | 1oo4 | DC Disconnector Rectifier 1&2 Row 1 - Feedback Fault | DC Disconnector feedback error | [6 empty] | S |  |  | N | [25 empty] | N | N |  |  | S |  |  |  | - All contactors and breakers of the power unit (2 power lines / half a row) are open excluding the discharge resistor contactor. - Logic implemented by internal IGBT system. - To be checked by Ingeteam if discharge resistor activation is accepted. - Command to connect discharge resistor and feedback is exchanged via Profinet and directly displayed at electrolyzer operator system - Trip all rectifiers because asynchronous operation is not allowed - Electrolyzer controller sends normal stop to both rectifier rows (both IC2 controllers). |  |  | V3.3, BM, 20240902: DC pre charge disconnectors QA13/33 were added
|  |  |  | G01NHA01QZ001-QA13 | GrpErr | - | 1 | - | BOOL | - | - | - | - |  | DC Disconnector Pre-Charge Rectifier 1&2 Row 1 - Feedback Fault
|  |  |  | G01NHA01QZ001-QA32 | GrpErr | - | 1 | - | BOOL | - | - | - | - |  | DC Disconnector Rectifier 3&4 Row 1 - Feedback Fault
|  |  |  | G01NHA01QZ001-QA33 | GrpErr | - | 1 | - | BOOL | - | - | - | - |  | DC Disconnector Pre-Charge Rectifier 3&4 Row 1 - Feedback Fault
|  |  | 3.3 | G01NHA01QZ002-QA12 | GrpErr | - | 1 | - | BOOL | - | - | - | - | 1oo4 | DC Disconnector Rectifier 1&2 Row 2 - Feedback Fault | [6 empty] | S |  |  |  |  | N | [26 empty] | N | N |  | S
|  |  |  | G01NHA01QZ002-QA13 | GrpErr | - | 1 | - | BOOL | - | - | - | - |  | DC Disconnector Pre-ChargeRectifier 1&2 Row 2 - Feedback Fault
|  |  |  | G01NHA01QZ002-QA32 | GrpErr | - | 1 | - | BOOL | - | - | - | - |  | DC Disconnector Rectifier 3&4 Row 2 - Feedback Fault
|  |  |  | G01NHA01QZ002-QA33 | GrpErr | - | 1 | - | BOOL | - | - | - | - |  | DC Disconnector Pre-Charge Rectifier 3&4 Row 2 - Feedback Fault
|  |  | 3.3 | G01NHA01TB001-KZ51 | XB01 | - | 1 | - | BOOL | - | 40/66 s for AH/ASHH | - | and | 2oo2 | Rectifier row 1 current control failure | 1= Pulses Enabled | [5 empty] | S | S | [36 empty] | Rectifier Control failure. Measured value of rectifier current differs to much from set point, while rectifier is in operation and not waiting for tap changer.
|  |  |  | G01NHA01TB001-KZ54 | XH52 | - | 0 | - | BOOL | - | [5 empty] | 0= Alpha G Limit not reached
|  |  |  | G01NHA01BZ011-KZ03 | XQ01 | AH ¦300.0¦ | ASHH ¦300.0¦ | 100.0 | A | - | [5 empty] | Delta between G01NHA01TB001-KZ21 and G01NHA01BZ001-BC02
|  |  | 3.3 | G01NHA01TB002-KZ51 | XB01 | - | 1 | - | BOOL | - | 40/66 s for AH/ASHH | - | and | 2oo2 | Rectifier row 2 current control failure | 1= Pulses Enabled | [5 empty] | S | S
|  |  |  | G01NHA01TB002-KZ54 | XH52 | - | 0 | - | BOOL | - | [5 empty] | 0= Alpha G Limit not reached
|  |  |  | G01NHA01BZ012-KZ03 | XQ01 | AH ¦300.0¦ | ASHH ¦300.0¦ | 100.0 | A | - | [5 empty] | Delta between G01NHA01TB002-KZ21 and G01NHA01BZ002-BC02
|  |  | 3.3 | G01NHA01QZ001-QA12 | XB01 | - | 0 | - | BOOL | - |  |  |  | 1oo2 | DC disconnector Rectifier Row1 DC Not ON (not closed) | DC disconnectors not closed | [39 empty] | S |  |  |  | Logic implementd by internal IGBT controller. Not all ACB of one row are opened, only ACBs of effected power line. Nevertheless all rows will be ramped down due to asymeetrical operation.
|  |  |  | G01NHA01QZ001-QA32 | XB01 | - | 0 | - | BOOL | -
|  |  | 3.3 | G01NHA01QZ002-QA12 | XB01 | - | 0 | - | BOOL | - |  |  |  | 1oo2 | DC disconnector Rectifier Row2 DC Not ON (not closed) | [41 empty] | S
|  |  |  | G01NHA01QZ002-QA32 | XB01 | - | 0 | - | BOOL | -
|  |  | 3.3 | G01NHA01QZ001-QA10 | XB01 | - | 0 | - | BOOL | - |  |  |  | 1oo1 | LV AC CB of converter system 1 Row 1 Not ON (not closed) | AC CB Row 1 not closed | [6 empty] | S |  |  | N | [25 empty] | N | N |  |  | S |  |  |  | - All contactors and breakers of the power unit (2 power lines / half a row) are open excluding the discharge resistor contactor. - Logic implemented by internal IGBT system. - To be checked by Ingeteam if discharge resitor activation is accepted. - Command to connect discharge resistor and feedback is exchanged via Profinet and directly displayed at electrolyzer operator system - Trip all rectifiers because asynchronous operation is not allowed - Electrolyzer controller sends normal stop to both rectifier rows (both IC2 controllers).
|  |  | 3.3 | G01NHA01QZ001-QA20 | XB01 | - | 0 | - | BOOL | - |  |  |  | 1oo1 | LV AC CB of converter system 2 Row 1 Not ON (not closed)
|  |  | 3.3 | G01NHA01QZ001-QA30 | XB01 | - | 0 | - | BOOL | - |  |  |  | 1oo1 | LV AC CB of converter system 3 Row 1 Not ON (not closed)
|  |  | 3.3 | G01NHA01QZ001-QA40 | XB01 | - | 0 | - | BOOL | - |  |  |  | 1oo1 | LV AC CB of converter system 4 Row 1 Not ON (not closed)
|  |  | 3.3 | G01NHA01QZ002-QA10 | XB01 | - | 0 | - | BOOL | - |  |  |  | 1oo1 | LV AC CB of converter system 1 Row 2 Not ON (not closed) | AC CB Row 2 not closed | [5 empty] | S |  |  |  |  | N | [26 empty] | N | N |  | S
|  |  | 3.3 | G01NHA01QZ002-QA20 | XB01 | - | 0 | - | BOOL | - |  |  |  | 1oo1 | LV AC CB of converter system 2 Row 2 Not ON (not closed)
|  |  | 3.3 | G01NHA01QZ002-QA30 | XB01 | - | 0 | - | BOOL | - |  |  |  | 1oo1 | LV AC CB of converter system 3 Row 2 Not ON (not closed)
|  |  | 3.3 | G01NHA01QZ002-QA40 | XB01 | - | 0 | - | BOOL | - |  |  |  | 1oo1 | LV AC CB of converter system 4 Row 2 Not ON (not closed)
|  |  | 3.3 | G01NHA01QZ001-QB11 | XB01 | - | 0 | - | BOOL | - |  |  |  | 1oo4 | AC CB Pre-Charge Rectifier Row1 Not OFF (not opened) | Pre-Charge AC CB row 1 not closed | [6 empty] | S |  |  | N | [25 empty] | N | N |  |  | S |  |  |  | - All contactors and breakers of the power unit (2 power lines / half a row) are open excluding the discharge resistor contactor. - Logic implemented by internal IGBT system. - To be checked by Ingeteam if discharge resitor activation is accepted. - Command to connect discharge resistor and feedback is exchanged via Profinet and directly displayed at electrolyzer operator system - Trip all rectifiers because asynchronous operation is not allowed - Electrolyzer controller sends normal stop to both rectifier rows (both IC2 controllers). |  |  | V3.3, BM,JS, BC, 20240903: new
|  |  |  | G01NHA01QZ001-QB21 | XB01 | - | 0 | - | BOOL | -
|  |  |  | G01NHA01QZ001-QB31 | XB01 | - | 0 | - | BOOL | -
|  |  |  | G01NHA01QZ001-QB41 | XB01 | - | 0 | - | BOOL | -
|  |  | 3.3 | G01NHA01QZ002-QB11 | XB01 | - | 0 | - | BOOL | - |  |  |  | 1oo4 | AC CB Pre-Charge Rectifier Row2 Not OFF (not opened) | Pre-Charge AC CB row 2 not closed | [5 empty] | S |  |  |  |  | N | [26 empty] | N | N |  | S
|  |  |  | G01NHA01QZ002-QB21 | XB01 | - | 0 | - | BOOL | -
|  |  |  | G01NHA01QZ002-QB31 | XB01 | - | 0 | - | BOOL | -
|  |  |  | G01NHA01QZ002-QB41 | XB01 | - | 0 | - | BOOL | -
|  |  | 3.3 | G01NHY01KF101/KZ12 | XB02 | - | 1 | - | BOOL | - |  |  |  | 1oo1 | Rectifier not off | 1 = Array in operation | [31 empty] | N | N | N | N | [8 empty] | 'Cause will lead to a sequence error
|  |  | 3.3N | G01NHA01TB001-KF101 | Err | - | - | - | - | - |  |  |  | 1oo1 | Command on step sequence error Monitoring of sequence steps Row 1 | [6 empty] | S | S | [36 empty] | - All contactors and breakers of the power unit (2 power lines / half a row) are open excluding the discharge resistor contactor. - Logic implemented by internal IGBT system. - To be checked by Ingeteam if discharge resistor activation is accepted. - Command to connect discharge resistor and feedback is exchanged via Profinet and directly displayed at electrolyzer operator system - Trip all rectifiers because asynchronous operation is not allowed - Electrolyzer controller sends normal stop to both rectifier rows (both IC2 controllers).
|  |  | 3.3N | G01NHA01TB001-KF102 | Err | - | - | - | - | - |  |  |  | 1oo1 | Command off step sequence error Monitoring of sequence steps Row 1 | [7 empty] | S | [32 empty] | S
|  |  | 3.3N | G01NHA01TB002-KF101 | Err | - | - | - | - | - |  |  |  | 1oo1 | Command on step sequence error Monitoring of sequence steps Row 2 | [6 empty] | S | S | [36 empty] | - All contactors and breakers of the power unit (2 power lines / half a row) are open excluding the discharge resistor contactor. - Logic implemented by internal IGBT system. - To be checked by Ingeteam if discharge resistor activation is accepted. - Command to connect discharge resistor and feedback is exchanged via Profinet and directly displayed at electrolyzer operator system - Trip all rectifiers because asynchronous operation is not allowed - Electrolyzer controller sends normal stop to both rectifier rows (both IC2 controllers).
|  |  | 3.3N | G01NHA01TB002-KF102 | Err | - | - | - | - | - |  |  |  | 1oo1 | Command off step sequence error Monitoring of sequence steps Row 2 | [6 empty] | S | [34 empty] | S
Note on AH9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No connection
Note on AH10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No Connection Reply: Checked by AS on 22042026 . Done
Note on BI43: Mahor, Abhishek (ext): TO be discussed with Bernd
Note on P194: Mahor, Abhishek (ext): Freeze protection to be discussed
Note on P245: Mahor, Abhishek (ext): Will be checked by Elec and conveyed the final understanding

## Ely System - Message only
Operational Messages without Protection Array X - Elyzer P-300 Reference Plant - has to be adjusted project specifically - | Operational Messages without Protection 1 Array - H2 Sakura - has to be adjusted project specifically -
| PLS# | Project Rev | Chgd | Input Tag | Signal | Warn | Alarm | Hyst. | Unit | W_DC | W_DG | Func 1 | Func 2 | Cause Description | Comment | Test date/result | Test executed by | Revision history /internal comments
Gas Analytic H2 side - NHC01BQ001-BQ01(discont.) | Gas Analytic H2 side - NHC01BQ001-BQ01(discont.)
#REF! |  | A | 3.1 | G01NHC01BQ001-QM23 | XB02 | 0 | - | - | BOOL | - | - |  | 1oo1 | Sensor 1 - Calibration active | indicated via message of -BQ01 | 24.04.2025 no change | F.Reinhart | V3.1, 2024-09-24 (FR): changed to 1oo1 and added comment for clarification
#REF! |  | A | 3.1 | G01NHC01BQ001-QM27 | XB02 | 0 | - | - | BOOL | - | - |  | 1oo1 | Sensor 2 - Calibration active | indicated via message of -BQ02 | 24.04.2025 no change | F.Reinhart | V3.1, 2024-09-24 (FR): changed to 1oo1 and added comment for clarification
#REF! |  | A | 3.3 | G01NHC01BQ001-BF01 | XG51 | 1 | - | - | BOOL | 10 s | - | and | 1oo1 | Sensor 1 - High Flow O2 in H2 | H 100.0 l/h (project specific adjustment needed), only enabled when system is filled with H2 and at least one measurement cycle of gas analytic was executed | 24.04.2025 implemented change | F.Reinhart | V3.1, 2024-09-24 (FR): changed to 1oo1 for clarification V3.3, 2025-04-24 (FR): enable message only when "Array -H2 Ready" for 640 s
#REF! |  | A |  | G01NHY01KF101/KZ100 |  | 1 | - | - | BOOL | 640 s | - |  |  | Array - H2 Ready
#REF! |  | A | 3.3 | G01NHC01BQ001-BF02 | XG51 | 1 | - | - | BOOL | 10 s | - | and | 1oo1 | Sensor 2 - High Flow O2 in H2 | H 100.0 l/h (project specific adjustment needed), only enabled when system is filled with H2 and at least one measurement cycle of gas analytic was executed | 24.04.2025 implemented change | F.Reinhart | V3.1, 2024-09-24 (FR): changed to 1oo1 for clarification V3.3, 2025-04-24 (FR): enable message only when "Array -H2 Ready" for 640 s
#REF! |  | A |  | G01NHY01KF101/KZ100 |  | 1 | - | - | BOOL | 640 s | - |  |  | Array - H2 Ready
#REF! |  | A | 3.1 | G01NHC01BQ001-BP10 | XQ01 | 80 | - | - | mbar | 10 s | - |  | 1oo1 | Monitoring of bellow Gaspump | project specific, monitoring of pump bellow, leak/ingress will increase O2 value | 24.04.2025 no change | F.Reinhart | V3.1, 2024-01-18, (BM): Switch changed to transmitter, warning at 80 mbarg
#REF! |  | A | 1.3 | G01NHC01BQ001-QN22 | XG02 | 0 | - | - | BOOL | 10 s | - |  | 1oo1 | Pressure Validation gas | L 10.0 Barg, project specific, can be defined by operator, based on bottle size and lead time | 24.04.2025 no change | F.Reinhart
#REF! |  | A | 1.3 | G01NHC01BQ001-BF10 | XG02 | 0 | - | - | BOOL | 10 s | - |  | 1oo1 | Flow "Fast Loop" O2 in H2 | L 100 l/h, project specific adjustment, 30m should cause Low Alarm at 150Nl/h | 24.04.2025 no change | F.Reinhart
#REF! |  | A | 1.3 | G01NHC01BQ001-FC01 | XU01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Circuit breaker feedback | Group fault alarm | 24.04.2025 no change | F.Reinhart
#REF! |  | A | 1.3 | G01NHC01BQ001-EQ01 | XU01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Gas Cooler -Fault | Group fault alarm | 24.04.2025 no change | F.Reinhart
#REF! |  | A | 3.3 | G01NHC01BQ001-KZ33 | XQ01 | - | ASH ¦1000.0¦ | 250.0 | Delta ppmV | - | - | - | 1oo1 | Delta Sensordrift O2 in H2 | saved measurement values -> delta of both sensors -> maximum evaluation (KZ33) | 24.04.2025 implemented change | F.Reinhart | V3.3, 2025-03-12 (FR+KB+RW): generate only warning message on delta drift and do not trigger validation, drift evaluation always enabled, hysteresis of 250 ppm
Gas Analytic O2 side - NHE01BQ001-BQ01 (discont.) | Gas Analytic O2 side - NHE01BQ001-BQ01 (discont.)
#REF! |  | A | 3.1 | G01NHE01BQ001-QM23 | XB02 | 0 | - | - | BOOL | - | - |  | 1oo1 | Sensor 1 - Calibration active | indicated via message of -BQ01 | 24.04.2025 no change | F.Reinhart | V3.1, 2024-09-24 (FR): changed to 1oo1 and added comment for clarification
#REF! |  | A | 3.1 | G01NHE01BQ001-QM27 | XB02 | 0 | - | - | BOOL | - | - |  | 1oo1 | Sensor 2 - Calibration active | indicated via message of -BQ02 | 24.04.2025 no change | F.Reinhart | V3.1, 2024-09-24 (FR): changed to 1oo1 and added comment for clarification
#REF! |  | A | 3.1 | G01NHE01BQ001-BF01 | XG51 | 1 | - | - | BOOL | 10 s | - |  | 1oo1 | Sensor 1 - High Flow H2 in O2 | H 100.0 l/h (project specific adjustment needed) | 24.04.2025 no change | F.Reinhart | V3.1, 2024-09-24 (FR): changed to 1oo1 for clarification
#REF! |  | A | 3.1 | G01NHE01BQ001-BF02 | XG51 | 1 | - | - | BOOL | 10 s | - |  | 1oo1 | Sensor 2 - High Flow H2 in O2 | H 100.0 l/h (project specific adjustment needed) | 24.04.2025 no change | F.Reinhart | V3.1, 2024-09-24 (FR): changed to 1oo1 for clarification
#REF! |  | A | 3.1 | G01NHE01BQ001-BP10 | XQ01 | 80 | - | - | mbar | 10 s | - |  | 1oo1 | Monitoring of bellow Gaspump | project specific, monitoring of pump bellow | 24.04.2025 no change | F.Reinhart | V3.1, 2024-01-18, (BM): Switch changed to transmitter, warning at 80 mbarg
#REF! |  | A | 1.3 | G01NHE01BQ001-QN22 | XG02 | 0 | - | - | BOOL | 10 s | - |  | 1oo1 | Pressure Validation gas | L 10.0 Barg, project specific, can be defined by operator, based on bottle size and lead time | 24.04.2025 no change | F.Reinhart
#REF! |  | A | 1.3 | G01NHE01BQ001-BF10 | XG02 | 0 | - | - | BOOL | 10 s | - |  | 1oo1 | Flow "Fast Loop" H2 in O2 | L 100 l/h, project specific adjustment, 30m should cause Low Alarm at 150Nl/h | 24.04.2025 no change | F.Reinhart
#REF! |  | A | 1.3 | G01NHE01BQ001-FC01 | XU01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Circuit breaker feedback | Group fault alarm | 24.04.2025 no change | F.Reinhart
#REF! |  | A | 1.3 | G01NHE01BQ001-EQ01 | XU01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Gas Cooler -Fault | Group fault alarm | 24.04.2025 no change | F.Reinhart
#REF! |  | A | 3.3 | G01NHE01BQ001-KZ33 | XQ01 | - | ASH ¦0.2¦ | 0.05 | Delta Vol % | - | - | - | 1oo1 | Delta Sensordrift H2 in O2 | saved measurement values -> delta of both sensors -> maximum evaluation (KZ33) | 24.04.2025 implemented change | F.Reinhart | V3.3, 2025-03-12 (FR+KB+RW): generate only warning message on delta drift and do not trigger validation, drift evaluation always enabled, hysteresis of 0.05 Vol%
Gas Separation | Gas Separation
#REF! |  | A | 2.0 | G01NHC01BL001-KZ11 | XQ01 | AH ¦3.0¦ | - | 2.0 | cm | 20 s | - |  | 1oo1 | Deviation Monitoring Level H2 | Delta between G01NHC01BL001-BL01 and G01NHC01BL001-BL02 | 25.04.2025 no change | F.Reinhart | V2.0 (FR): only adapted tag KZ11, which is the delta evaluation of the two sensors in the software
#REF! |  | A | 2.0 | G01NHE01BL001-KZ11 | XQ01 | AH ¦3.0¦ | - | 2.0 | cm | 20 s | - |  | 1oo1 | Deviation Monitoring Level O2 | Delta between G01NHE01BL001-BL01 and G01NHE01BL001-BL02 | 25.04.2025 no change | F.Reinhart | V2.0 (FR): only adapted tag KZ11, which is the delta evaluation of the two sensors in the software
#REF! |  | A | 2.0 | G01NHC01HP001-KZ11 | XQ01 | AH ¦12.0¦ | - | 5.0 | mbar | 5 s | - |  | 1oo1 | Deviation Monitoring Pressure H2 | Delta between G01NHC01HP001-BP01 and G01NHC01HP001-BP02 | 25.04.2025 no change | F.Reinhart | V2.0 (FR): only adapted tag KZ11, which is the delta evaluation of the two sensors in the software
#REF! |  | A | 2.0 | G01NHE01HP001-KZ11 | XQ01 | AH ¦12.0¦ | - | 5.0 | mbar | 5 s | - |  | 1oo1 | Deviation Monitoring Pressure O2 | Delta between G01NHE01HP001-BP01 and G01NHE01HP001-BP02 | 25.04.2025 no change | F.Reinhart | V2.0 (FR): only adapted tag KZ11, which is the delta evaluation of the two sensors in the software
|  | A | 3.3 | G01NHC01HP001-BP02 | XQ01 | AH 140.0 | - | 5.0 | mbar(g) | - | - |  | 1oo1 | High Pressure H2 |  | 24.04.2025 implemented change | F.Reinhart | V3.0, BM, JS, 30.10.2023: Druck hoch wurde gelöscht um mehr betrieblichen Spielraum zu bekommen. Bei einem plötzlichen Druckanstieg würde eine Druck hoch Abschaltung sowieso zum Druck hoch SIS und Ansprechen des PSV führen. Deshalb nur SIS Abschaltung, welche ein dauerhaftes Abblase verhindert. V3.3, FR, 24.04.2025: moved from operational trips to message only
|  | A | 3.3 | G01NHE01HP001-BP02 | XQ01 | AH 140.0 | - | 5.0 | mbar(g) | - | - |  | 1oo1 | High Pressure O2 |  | 24.04.2025 implemented change | F.Reinhart | V3.0, BM, JS, 30.10.2023: Druck hoch wurde gelöscht um mehr betrieblichen Spielraum zu bekommen. Bei einem plötzlichen Druckanstieg würde eine Druck hoch Abschaltung sowieso zum Druck hoch SIS und Ansprechen des PSV führen. Deshalb nur SIS Abschaltung, welche ein dauerhaftes Abblase verhindert. V3.3, FR, 24.04.2025: moved from operational trips to message only
#REF! |  | A | 1.3 | G01NHC01GT001-QN01 | XU01 | 0 |  |  | BOOL |  |  |  | 1oo1 |  | Group fault alarm | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.3 | G01NHC01GT001-QN02 | XU01 | 0 |  |  | BOOL |  |  |  | 1oo1 |  | Group fault alarm | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.3 | G01NHE01GT001-QN01 | XU01 | 0 |  |  | BOOL |  |  |  | 1oo1 |  | Group fault alarm | 25.04.2025 no change | F.Reinhart
Cell Voltage | Cell Voltage
|  | A |  | G01NHB01HT001-KZ13 (max.) |  | XQ01 | AH (G01NHB01HT001-KZ14 (avg.) +0.2) | 0.1 | V | 5min | - |  | 1oo1 | High Cell Voltage SG 1 Stack 1
|  | A |  | G01NHB01HT001-KZ12 (min.) |  | XQ01 | AL (G01NHB01HT001-KZ14 (avg.) -0.2) | 0.1 | V | 5min | - |  | 1oo1 | Low Cell Voltage SG 1 Stack 1
|  | A |  | G01NHB01HT002-KZ13 (max.) |  | XQ01 | AH (G01NHB01HT002-KZ14 (avg.) +0.2) | 0.1 | V | 5min | - |  | 1oo1 | High Cell Voltage SG 1 Stack 2
|  | A |  | G01NHB01HT002-KZ12 (min.) |  | XQ01 | AL (G01NHB01HT002-KZ14 (avg.) -0.2) | 0.1 | V | 5min | - |  | 1oo1 | Low Cell Voltage SG 1 Stack 2
|  | A |  | G01NHB01HT003-KZ13 (max.) |  | XQ01 | AH (G01NHB01HT003-KZ14 (avg.) +0.2) | 0.1 | V | 5min | - |  | 1oo1 | High Cell Voltage SG 1 Stack 3
|  | A |  | G01NHB01HT003-KZ12 (min.) |  | XQ01 | AL (G01NHB01HT003-KZ14 (avg.) -0.2) | 0.1 | V | 5min | - |  | 1oo1 | Low Cell Voltage SG 1 Stack 3
|  | A |  | G01NHB01HT004-KZ13 (max.) |  | XQ01 | AH (G01NHB01HT004-KZ14 (avg.) +0.2) | 0.1 | V | 5min | - |  | 1oo1 | High Cell Voltage SG 1 Stack 4
|  | A |  | G01NHB01HT004-KZ12 (min.) |  | XQ01 | AL (G01NHB01HT004-KZ14 (avg.) -0.2) | 0.1 | V | 5min | - |  | 1oo1 | Low Cell Voltage SG 1 Stack 4
|  | A |  | G01NHB02HT001-KZ13 (max.) |  | XQ01 | AH (G01NHB02HT001-KZ14 (avg.) +0.2) | 0.1 | V | 5min | - |  | 1oo1 | High Cell Voltage SG 2 Stack 1
|  | A |  | G01NHB02HT001-KZ12 (min.) |  | XQ01 | AL (G01NHB02HT001-KZ14 (avg.) -0.2) | 0.1 | V | 5min | - |  | 1oo1 | Low Cell Voltage SG 2 Stack 1
|  | A |  | G01NHB02HT002-KZ13 (max.) |  | XQ01 | AH (G01NHB02HT002-KZ14 (avg.) +0.2) | 0.1 | V | 5min | - |  | 1oo1 | High Cell Voltage SG 2 Stack 2
|  | A |  | G01NHB02HT002-KZ12 (min.) |  | XQ01 | AL (G01NHB02HT002-KZ14 (avg.) -0.2) | 0.1 | V | 5min | - |  | 1oo1 | Low Cell Voltage SG 2 Stack 2
|  | A |  | G01NHB02HT003-KZ13 (max.) |  | XQ01 | AH (G01NHB02HT003-KZ14 (avg.) +0.2) | 0.1 | V | 5min | - |  | 1oo1 | High Cell Voltage SG 2 Stack 3
|  | A |  | G01NHB02HT003-KZ12 (min.) |  | XQ01 | AL (G01NHB02HT003-KZ14 (avg.) -0.2) | 0.1 | V | 5min | - |  | 1oo1 | Low Cell Voltage SG 2 Stack 3
|  | A |  | G01NHB02HT004-KZ13 (max.) |  | XQ01 | AH (G01NHB02HT00-KZ14 (avg.) +0.2) | 0.1 | V | 5min | - |  | 1oo1 | High Cell Voltage SG 2 Stack 4
|  | A |  | G01NHB02HT004-KZ12 (min.) |  | XQ01 | AL (G01NHB02HT004-KZ14 (avg.) -0.2) | 0.1 | V | 5min | - |  | 1oo1 | Low Cell Voltage SG 2 Stack 4
|  | A |  | … |  | XQ01 | AH (avg. +0.2) | 0.1 | V | 5min | - |  | 1oo1 | …
|  | A |  | … |  | XQ01 | AL (avg. -0.2) | 0.1 | V | 5min | - |  | 1oo1 | …
|  | A |  | G01NHB06HT004-KZ13 (max.) |  | XQ01 | AH (G01NHB06HT004-KZ14 (avg.) +0.2) | 0.1 | V | 5min | - |  | 1oo1 | High Cell Voltage SG 6 Stack 4
|  | A |  | G01NHB06HT004-KZ12 (min.) |  | XQ01 | AL (G01NHB06HT004-KZ14 (avg.) -0.2) | 0.1 | V | 5min | - |  | 1oo1 | Low Cell Voltage SG 6 Stack 4
Module Temperatures | Module Temperatures
Module Temperatures |  | A | 3.3 | G01NHB01HT001-KZ11 | XQ01 | AH ¦5.0¦ | - | 1.0 | °C | 5 min | - |  | 1oo1 | diff. Temp. outlet Module 1 / Group 1 | Delta between G01NHB01HT001-BT01 and G01NHB01HT001-BT02 (only enabled, when Array is in operation and Stack Row1&2 is enabled) | 23.04.2025 implemented change | F. Reinhart | V2.0 (FR): only adapted tag KZ11, which is the delta evaluation of the two sensors in the software V3.1,V2.1 (KB): During Standstill the Temperaturedeviation will increase due to the water refinement. Because of this it was decided to only enable this function when the array is in operation and the delay time has been increased to 2min. V3.3, BM, FR, 2024-07-19: delay coming increased from 2 to 5 min, since during start up there can still be deviations caused by different temp. during standstill, which are not critical.value increased form 2 to 3K to set back warning with hysterisis of 1 K. FR, 2024-09-24: warnings should only be enabled, when array is in operation and according Stack Row is enabled KB, BM, 2025-02-07: limit changed from 3 to 5 K, based on temperature deviation during normal operation (~2-3 K, due to influence of water refinement)
#REF! |  | A
#REF! |  | A | 3.3 | G01NHB01HT002-KZ11 | XQ01 | AH ¦5.0¦ | - | 1.0 | °C | 5 min | - |  | 1oo1 | diff. Temp. outlet Module 2 / Group 1 | Delta between G01NHB01HT002-BT01 and G01NHB01HT002-BT02 (only enabled, when Array is in operation and Stack Row1&2 is enabled) | 23.04.2025 implemented change | F. Reinhart
#REF! |  | A
#REF! |  | A | 3.3 | G01NHB01HT003-KZ11 | XQ01 | AH ¦5.0¦ | - | 1.0 | °C | 5 min | - |  | 1oo1 | diff. Temp. outlet Module 3 / Group 1 | Delta between G01NHB01HT003-BT01 and G01NHB01HT003-BT02 (only enabled, when Array is in operation and Stack Row3&4 is enabled) | 23.04.2025 implemented change | F. Reinhart
#REF! |  | A
#REF! |  | A | 3.3 | G01NHB01HT004-KZ11 | XQ01 | AH ¦5.0¦ | - | 1.0 | °C | 5 min | - |  | 1oo1 | diff. Temp. outlet Module 4 / Group 1 | Delta between G01NHB01HT004-BT01 and G01NHB01HT004-BT02 (only enabled, when Array is in operation and Stack Row3&4 is enabled) | 23.04.2025 implemented change | F. Reinhart
#REF! |  | A
#REF! |  | A | 3.3 | G01NHB02HT001-KZ11 | XQ01 | AH ¦5.0¦ | - | 1.0 | °C | 5 min | - |  | 1oo1 | diff. Temp. outlet Module 1 / Group 2 | Delta between G01NHB02HT001-BT01 and G01NHB02HT001-BT02 (only enabled, when Array is in operation and Stack Row1&2 is enabled) | 23.04.2025 implemented change | F. Reinhart
#REF! |  | A
#REF! |  | A | 3.3 | G01NHB02HT002-KZ11 | XQ01 | AH ¦5.0¦ | - | 1.0 | °C | 5 min | - |  | 1oo1 | diff. Temp. outlet Module 2 / Group 2 | Delta between G01NHB02HT002-BT01 and G01NHB02HT002-BT02 (only enabled, when Array is in operation and Stack Row1&2 is enabled) | 23.04.2025 implemented change | F. Reinhart
#REF! |  | A
#REF! |  | A | 3.3 | G01NHB02HT003-KZ11 | XQ01 | AH ¦5.0¦ | - | 1.0 | °C | 5 min | - |  | 1oo1 | diff. Temp. outlet Module 3 / Group 2 | Delta between G01NHB02HT003-BT01 and G01NHB02HT003-BT02 (only enabled, when Array is in operation and Stack Row3&4 is enabled) | 23.04.2025 implemented change | F. Reinhart
#REF! |  | A
#REF! |  | A | 3.3 | G01NHB02HT004-KZ11 | XQ01 | AH ¦5.0¦ | - | 1.0 | °C | 5 min | - |  | 1oo1 | diff. Temp. outlet Module 4 / Group 2 | Delta between G01NHB02HT004-BT01 and G01NHB02HT004-BT02 (only enabled, when Array is in operation and Stack Row3&4 is enabled) | 23.04.2025 implemented change | F. Reinhart
#REF! |  | A
#REF! |  | A | 3.3 | … | XQ01 | AH ¦5.0¦ | - | 1.0 | °C | 5 min | - |  | 1oo1 | … | … | 23.04.2025 implemented change | F. Reinhart
#REF! |  | A
#REF! |  | A | 3.3 | G01NHB06HT001-KZ11 | XQ01 | AH ¦5.0¦ | - | 1.0 | °C | 5 min | - |  | 1oo1 | diff. Temp. outlet Module 1 / Group 6 | Delta between G01NHB06HT001-BT01 and G01NHB06HT001-BT02 (only enabled, when Array is in operation and Stack Row1&2 is enabled) | 23.04.2025 implemented change | F. Reinhart
#REF! |  | A
#REF! |  | A | 3.3 | G01NHB06HT002-KZ11 | XQ01 | AH ¦5.0¦ | - | 1.0 | °C | 5 min | - |  | 1oo1 | diff. Temp. outlet Module 2 / Group 6 | Delta between G01NHB06HT002-BT01 and G01NHB06HT002-BT02 (only enabled, when Array is in operation and Stack Row1&2 is enabled) | 23.04.2025 implemented change | F. Reinhart
#REF! |  | A
#REF! |  | A | 3.3 | G01NHB06HT003-KZ11 | XQ01 | AH ¦5.0¦ | - | 1.0 | °C | 5 min | - |  | 1oo1 | diff. Temp. outlet Module 3 / Group 6 | Delta between G01NHB06HT003-BT01 and G01NHB06HT003-BT02 (only enabled, when Array is in operation and Stack Row3&4 is enabled) | 23.04.2025 implemented change | F. Reinhart
#REF! |  | A
#REF! |  | A | 3.3 | G01NHB06HT004-KZ11 | XQ01 | AH ¦5.0¦ | - | 1.0 | °C | 5 min | - |  | 1oo1 | diff. Temp. outlet Module 4 / Group 6 | Delta between G01NHB06HT004-BT01 and G01NHB06HT004-BT02 (only enabled, when Array is in operation and Stack Row3&4 is enabled) | 23.04.2025 implemented change | F. Reinhart
#REF! |  | A
Conductivity Process Water Module Groups | Conductivity Process Water Module Groups
Conductivity Process Water Module Groups |  | A | 2.0 | G01NHB01EQ001-BQ01 | XQ01 | AH 3.0 | - | 1.0 | µS/cm | 5 min | - |  | 1oo1 | Conductivity Monitoring SG1 H2 side |  | 23.04.2025 no change | F.Reinhart | V2.0 (FR): use 1oo1 for each stack group instead of 1oo6, no functional change
Conductivity Process Water Module Groups |  | A | 2.0 | G01NHB02EQ001-BQ01 | XQ01 | AH 3.0 | - | 1.0 | µS/cm | 5 min | - |  | 1oo1 | Conductivity Monitoring SG2 H2 side |  | 23.04.2025 no change | F.Reinhart | V2.0 (FR): use 1oo1 for each stack group instead of 1oo6, no functional change
Conductivity Process Water Module Groups |  | A | 2.0 | G01NHB03EQ001-BQ01 | XQ01 | AH 3.0 | - | 1.0 | µS/cm | 5 min | - |  | 1oo1 | Conductivity Monitoring SG3 H2 side |  | 23.04.2025 no change | F.Reinhart | V2.0 (FR): use 1oo1 for each stack group instead of 1oo6, no functional change
Conductivity Process Water Module Groups |  | A | 2.0 | G01NHB04EQ001-BQ01 | XQ01 | AH 3.0 | - | 1.0 | µS/cm | 5 min | - |  | 1oo1 | Conductivity Monitoring SG4 H2 side |  | 23.04.2025 no change | F.Reinhart | V2.0 (FR): use 1oo1 for each stack group instead of 1oo6, no functional change
Conductivity Process Water Module Groups |  | A | 2.0 | G01NHB05EQ001-BQ01 | XQ01 | AH 3.0 | - | 1.0 | µS/cm | 5 min | - |  | 1oo1 | Conductivity Monitoring SG5 H2 side |  | 23.04.2025 no change | F.Reinhart | V2.0 (FR): use 1oo1 for each stack group instead of 1oo6, no functional change
Conductivity Process Water Module Groups |  | A | 2.0 | G01NHB06EQ001-BQ01 | XQ01 | AH 3.0 | - | 1.0 | µS/cm | 5 min | - |  | 1oo1 | Conductivity Monitoring SG6 H2 side |  | 23.04.2025 no change | F.Reinhart | V2.0 (FR): use 1oo1 for each stack group instead of 1oo6, no functional change
Conductivity Process Water Module Groups |  | A | 2.0 | G01NHB01EQ001-BQ02 | XQ01 | AH 3.0 | - | 1.0 | µS/cm | 5 min | - |  | 1oo1 | Conductivity Monitoring SG1 O2 side |  | 23.04.2025 no change | F.Reinhart | V2.0 (FR): use 1oo1 for each stack group instead of 1oo6, no functional change
Conductivity Process Water Module Groups |  | A | 2.0 | G01NHB02EQ001-BQ02 | XQ01 | AH 3.0 | - | 1.0 | µS/cm | 5 min | - |  | 1oo1 | Conductivity Monitoring SG2 O2 side |  | 23.04.2025 no change | F.Reinhart | V2.0 (FR): use 1oo1 for each stack group instead of 1oo6, no functional change
Conductivity Process Water Module Groups |  | A | 2.0 | G01NHB03EQ001-BQ02 | XQ01 | AH 3.0 | - | 1.0 | µS/cm | 5 min | - |  | 1oo1 | Conductivity Monitoring SG3 O2 side |  | 23.04.2025 no change | F.Reinhart | V2.0 (FR): use 1oo1 for each stack group instead of 1oo6, no functional change
Conductivity Process Water Module Groups |  | A | 2.0 | G01NHB04EQ001-BQ02 | XQ01 | AH 3.0 | - | 1.0 | µS/cm | 5 min | - |  | 1oo1 | Conductivity Monitoring SG4 O2 side |  | 23.04.2025 no change | F.Reinhart | V2.0 (FR): use 1oo1 for each stack group instead of 1oo6, no functional change
Conductivity Process Water Module Groups |  | A | 2.0 | G01NHB05EQ001-BQ02 | XQ01 | AH 3.0 | - | 1.0 | µS/cm | 5 min | - |  | 1oo1 | Conductivity Monitoring SG5 O2 side |  | 23.04.2025 no change | F.Reinhart | V2.0 (FR): use 1oo1 for each stack group instead of 1oo6, no functional change
Conductivity Process Water Module Groups |  | A | 2.0 | G01NHB06EQ001-BQ02 | XQ01 | AH 3.0 | - | 1.0 | µS/cm | 5 min | - |  | 1oo1 | Conductivity Monitoring SG6 O2 side |  | 23.04.2025 no change | F.Reinhart | V2.0 (FR): use 1oo1 for each stack group instead of 1oo6, no functional change
Cooling Circuit Modulgroups | Cooling Circuit Modulgroups
Cooling Circuit Modulgroups |  | A | 1.3 | G01NHB01EQ001-QN01 | XU01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Control valve - Module group 1 | Group fault alarm | 23.04.2025 no change | F.Reinhart
Cooling Circuit Modulgroups |  | A | 1.3 | G01NHB02EQ001-QN01 | XU01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Control valve - Module group 2 | Group fault alarm | 23.04.2025 no change | F.Reinhart
Cooling Circuit Modulgroups |  | A | 1.3 | G01NHB03EQ001-QN01 | XU01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Control valve - Module group 3 | Group fault alarm | 23.04.2025 no change | F.Reinhart
Cooling Circuit Modulgroups |  | A | 1.3 | G01NHB04EQ001-QN01 | XU01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Control valve - Module group 4 | Group fault alarm | 23.04.2025 no change | F.Reinhart
Cooling Circuit Modulgroups |  | A | 1.3 | G01NHB05EQ001-QN01 | XU01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Control valve - Module group 5 | Group fault alarm | 23.04.2025 no change | F.Reinhart
Cooling Circuit Modulgroups |  | A | 1.3 | G01NHB06EQ001-QN01 | XU01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Control valve - Module group 6 | Group fault alarm | 23.04.2025 no change | F.Reinhart
Control Unit - Module Groups | Control Unit - Module Groups
#REF! |  | A | 1.3 | G01NHB0xKF001-FC0x | XW01 | 0 |  |  | BOOL |  |  |  | 1oo1 | 24VDC Distribution - feedback | Group fault alarm | 23.04.2025 no change | F.Reinhart
#REF! |  | A | 1.3 | G01NHB0xKF001-TB0x | XW01 | 0 |  |  | BOOL |  |  |  | 1oo1 | 24VDC Generation - feedback | Group fault alarm | 23.04.2025 no change | F.Reinhart
Gas Temperatures | Gas Temperatures
Gas Temperatures |  | A | 1.1 | G01NHC01HP001-BT01 | XQ01 | AH 68.0 | - | 1.0 | °C | 5 s | - |  | 1oo1 | Temp. HX in |  | 23.04.2025 no change | F.Reinhart
Gas Temperatures |  | A | 1.1 | G01NHC01GT001-BT01 | XQ01 | AH 45.0 | - | 1.0 | °C | 5 s | - |  | 1oo1 | Temp. HX out | Values and Limit project specific (downstream gas system) | 23.04.2025 no change | F.Reinhart
Gas Temperatures |  | A | 1.1 | G01NHE01HP001-BT01 | XQ01 | AH 68.0 | - | 1.0 | °C | 5 s | - |  | 1oo1 | Temp. HX in |  | 23.04.2025 no change | F.Reinhart
Gas Temperatures |  | A | 1.1 | G01NHE01GT001-BT01 | XQ01 | AH 45.0 | - | 1.0 | °C | 5 s | - |  | 1oo1 | Temp. HX out |  | 23.04.2025 no change | F.Reinhart
Water Supply System | Water Supply System
#REF! |  | A | 1.3 | G01NHG01QM001-QN01 | XU01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Control valve - Demin water supply | Group fault alarm | 23.04.2025 no change | F.Reinhart
Water Refinement | Water Refinement
#REF! |  | A | 3.3 | G01NHH01HP001-KF92 | XQ01 | AH (SP+5%) AL (SP-5%) | - | - | % | 60 s | - |  | 2oo2 | Flowdistribution Refinement | Control error warning, when process value (=G01NHH01HP001-BF30) is deviating too much from setpoint and Split Rate Control (KZ50) enabled | 25.04.2025 implemented change | F. Reinhart | V3.1, FR, 2024-09-24: changed BF30 to KF92, because the message is generated by the PID controller V3.3, KB, 2025-04-03: KZ50 added to specify that this is only active when Split Rate Control enabled
|  | A |  | G01NHH01KF201-KZ50 | - | 1 | - | - | BOOL
Gas Temperatures |  | A | 1.3 | G01NHH01HP001-BQ01 | XQ02 | AH 65.0 |  |  | °C | 10 s |  |  | 1oo1 | Temperature - Water Refinement loop |  | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 3.3 | G01NHH01HP001-BQ02 | XQ01 | AH 0.2 | AHH 0.5 | 0.05 | µS/cm | 10 s | - | - | 1oo1 | Ion Exchanger Row 1 - High Conductivity | Pre-Warning at 0,2 to exchange the ion exchanger the next 3 days. Warning with higher Priority at 0,5 to exchange Ion exchanger immediatelly. Warnings and/or alarms are only valid if refinement pumps are running. | 25.04.2025 implemented change | F.Reinhart | V3.0, BM, 07.11.2023: comment changed: "minimum" corrected to "maximum"; "Warnings and/or alarms are only valid if refinement pumps are running." V3.3, FR, 25.04.2025: split into two separate causes, there should be no 2oo2 or maximum evaluation. If there is a second conductivity measurement, each sensor will give a warning message on the high limit
#REF! |  | A | 3.3 | G01NHH01HP001-BQ03 (optional) | XQ01 | AH 0.2 | AHH 0.5 | 0.05 | µS/cm | 10 s | - | - | 1oo1 | Ion Exchanger Row 2 - High Conductivity | Pre-Warning at 0,2 to exchange the ion exchanger the next 3 days. Warning with higher Priority at 0,5 to exchange Ion exchanger immediatelly. Warnings and/or alarms are only valid if refinement pumps are running. | 25.04.2025 implemented change | F.Reinhart | V3.0, BM, 07.11.2023: comment changed: "minimum" corrected to "maximum"; "Warnings and/or alarms are only valid if refinement pumps are running." V3.3, FR, 25.04.2025: split into two separate causes, there should be no 2oo2 or maximum evaluation. If there is a second conductivity measurement, each sensor will give a warning message on the high limit
#REF! |  | A | 3.3 | G01NHH01HP001-BP02 | XQ01 | AH 5.8 | - | 0.1 | bar(g) | 10 s | - |  | 1oo1 | Refinement Pump - High Pressure | Warning at shall be 0,5 bar higher than pressure with new filter at nominal flow. To be adjusted during comissioning. | 25.04.2025 implemented change | F.Reinhart | V.3.2, BM, 2024-05-15: changed from 3 to 4,2 barg. Comment changed. V3.3,BM, Cause description changed from "Refinement Filter - High Differential Pressure" to " Refinement Pump - High Pressure"
N2 Supply | N2 Supply
#REF! |  | A | 3.3 | G01NHX01QN001-BP01 | XQ01 | AH 2.0 | - | 0.2 | bar(g) | 10 s | 60 s |  | 1oo2 | N2 Supply - Pressure High | Values to be checked project specific | 25.04.2025 already implemented | F. Reinhart | V3.1, V2.1 (KB): added delay coming. When N2 manual valve gets opened, the pressure will overshoot and warning will stay active because of hysteresis V3.3, V3.1, 2024-10-29: Warning limit increased from 1,6 to 2,0 barg in order to not run in unintended warning every time when N2 purge starts
#REF! |  | A |  | G01NHX01QN002-BP01 | XQ01 | H 1.6 | - | 0.2 | bar(g) | - | 60 s |  |  | N2 Supply Separator/Header | Values project specific
#REF! |  | A | 3.1 | G01NHX01QN001-KZ11 | XQ01 | AH ¦0.2¦ | - | 0.1 | bar(g) | 10 s | 60 s |  | 1oo1 | N2 Supply - Delta Pressure High | Delta between G01NHX01QN001-BP01 and G01NHX01QN002-BP01 Values project specific | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.4 | G01NHX01QN001-BF01 | XQ01 | AL 600.0 | - | 10.0 | Nm³/h | 30 s |  |  | 2oo2 | Flowmeter - Nitrogen H2 side | Low N2 Flow during purge of H2 side | 25.04.2025 no change | F.Reinhart
#REF! |  | A |  | G01NHX01KF201-KZ55 |  | 1 | - | - | BOOL |  |  |  |  | N2 System - N2 Purge H2 side
#REF! |  | A | 1.3 | G01NHX01QN001-QN01 | XU01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Control Valve - Nitrogen H2 side | Group fault alarm | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.4 | G01NHX01QN002-BF02 | XQ01 | AL 600.0 | - | 10.0 | Nm³/h | 30 s |  |  | 2oo2 | Flowmeter - Nitrogen O2 side | Low N2 Flow during purge of O2 side | 25.04.2025 no change | F.Reinhart
#REF! |  | A |  | G01NHX01KF201-KZ56 |  | 1 | - | - | BOOL |  |  |  |  | N2 System - N2 Purge O2 side
#REF! |  | A | 1.3 | G01NHX01QN002-QN01 | XU01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Control Valve - Nitrogen O2 side | Group fault alarm | 25.04.2025 no change | F.Reinhart
Array Control System | Array Control System
Array Control System |  | A | 1.3 | G01NHY01KF001-BAxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Voltage monitoring | feedback, Note remarkt obe added as per IO list | 25.04.2025 must be checked again for each signal | F.Reinhart
Array Control System |  | A | 1.3 | G01NHY01KF001-FCxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Circuit breaker feedback | feedback, Note remarkt obe added as per IO list | 25.04.2025 must be checked again for each signal | F.Reinhart
Array Control System |  | A | 1.3 | G01NHY01KF001-QAxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Circuit breaker feedback | feedback, Note remarkt obe added as per IO list | 25.04.2025 must be checked again for each signal | F.Reinhart
Array Control System |  | A | 1.3 | G01NHY01KF001-TBxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | 24VDC generation feedback | feedback, Note remarkt obe added as per IO list | 25.04.2025 must be checked again for each signal | F.Reinhart
Array Control System |  | A | 3.3 | G01NHY01KF001-KZ61 |  | 0 |  |  | BOOL |  |  |  | 1oo1 | CPU Power Supply Module 1 - Available | Module State is evaluated in the Software via "Read System State Blocks". Waning is issued if one of the redundant power supplies is not available. |  |  | V3.3, KB, 20.08.2025: Created entry
Array Control System |  | A | 3.3 | G01NHY01KF001-KZ62 |  | 0 |  |  | BOOL |  |  |  | 1oo1 | CPU Power Supply Module 2 - Available | Module State is evaluated in the Software via "Read System State Blocks". Waning is issued if one of the redundant power supplies is not available. |  |  | V3.3, KB, 20.08.2025: Created entry
Heat Dissipation System | Heat Dissipation System
Heat Dissipation System |  | A | 3.3 | G01NHP01WP001-BT01 | XQ01 | AL 2.0 |  |  | °C | 5 min |  |  | 1oo1 | Temperature - WCR Gas Cooler H2 | Optional and project specific: Only necessary for cooling water with potential of freezing | 13.05.2025 implemented change | F.Reinhart | V3.3, BM: Warning high at 45°C changed to warning low 2°C , DC 5min in case of cw with freeze potetial
Heat Dissipation System |  | A | 3.3 | G01NHP01WP001-BT02 | XQ01 | AL 2.0 |  |  | °C | 5 min |  |  | 1oo1 | Temperature - WCR Gas Cooler O2 | Optional and project specific: Only necessary for cooling water with potential of freezing | 13.05.2025 implemented change | F.Reinhart | V3.3, BM: Warning high at 45°C changed to warning low 2°C , DC 5min in case of cw with freeze potetial
Heat Dissipation System |  | A | 1.3 | G01NHP01WP001-QN01 | XU01 | 1 |  |  | BOOL |  |  |  | 1oo1 | Control Valve - Gas Cooler H2 Cooling Water | Group fault alarm | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.3 | G01NHP01WP001-QN02 | XU01 | 1 |  |  | BOOL |  |  |  | 1oo1 | Control Valve - Gas Cooler O2 Cooling Water | Group fault alarm | 25.04.2025 no change | F.Reinhart
Transformer (Customer's scope) | Transformer (Customer's scope)
Transformer (Customer's scope) |  | A | 1.2 | G01NHA01TA001-BU01 | XM01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Buchholzrelay AL1 |  | 25.04.2025 no change | F.Reinhart
Transformer (Customer's scope) |  | A | 1.1 | G01NHA01TA001-BT01 | XM01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Oil Temp. Transformer Alarm 1 |  | 25.04.2025 no change | F.Reinhart
|  | A | 3.3 | G01NHA01TA001-BT20 | XQ01 | AH 40.0 |  | 2.0 | °C | 5 s |  |  | 1oo1 | Cooling Water inlet | Optional | 25.04.2025 no change | F.Reinhart | V3.3, Nemanja, BM, 2024.12.11: "only optional added"
|  | A | 3.3 | G01NHA01TA001-BT21 | XQ01 | AH 45.0 |  | 2.0 | °C | 5 s |  |  | 1oo1 | Cooling Water outlet | Optional | 25.04.2025 no change | F.Reinhart | V3.3, Nemanja, BM, 2024.12.11: "only optional added"
#REF! |  | A | 1.2 | G01NHA01TA001-BT02 | XM01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Winding Temperature Transformer Al1 |  | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.1 | G01NHA01TA001-BL01 | XM01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Oil Level Min |  | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.1 | G01NHA01TA001-BL01 | XM02 | 0 | - | - | BOOL | - | - |  | 1oo1 | Oil Level Max |  | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.2 | G01NHA01TA001-BL02 | XM01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Transformer leakage level high |  | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.2 | G01NHA01TA001-BL03 | XM01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Tap changer oil Level Min |  | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.2 | G01NHA01TA001-BL03 | XM02 | 0 | - | - | BOOL | - | - |  | 1oo1 | Tap changer oil Level Max |  | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.1 | G01NHA01TA001-BF01 | XM01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Oil Circulation Alarm 1 |  | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 3.3 | G01NHA01TA001-BF02 | XM01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Cooling Flow Alarm 1 | Optional | 25.04.2025 no change | F.Reinhart | V3.3, Nemanja, BM, 2024.12.11: "only optional added"
#REF! |  | A | 1.2 | G01NHA01TA001-FC01 | XM01 | 1 | - | - | BOOL | - | - |  | 1oo1 | Overcurrent protection pickup |  | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.3 | G01NHA01TA001-FC01 | XU01 | 1 | - | - | BOOL | - | - |  | 1oo1 | Overcurrent protection - Fault | Group fault alarm | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.2 | G01NHA01TA001-FC02 | XM01 | 1 | - | - | BOOL | - | - |  | 1oo1 | Overcurrent protection pickup |  | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.3 | G01NHA01TA001-FC02 | XU01 | 1 | - | - | BOOL | - | - |  | 1oo1 | Overcurrent protection - Fault | Group fault alarm | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.3 | G01NHA01TA001-GP01 | XB13 | 1 | - | - | BOOL | - | - |  | 1oo1 | Oil pump not running | Only active if rectifier current > 100 A DC | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.4 | G01NHA01TA001-QA02 | XR01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Tap changer not running | Feedback - Main Circuit Breaker ON | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.4 | G01NHA01TA001-QA02 | XB07 | 0 | - | - | BOOL | - | - |  | 1oo1 | Tap changer - not Remote |  | 25.04.2025 no change | F.Reinhart
Rectifier (Customer's scope) | Rectifier (Customer's scope)
#REF! |  | A | 3.0 | G01NHA01EQ001-BQ01 | XQ02 | AH 48.0 | - | 2.0 | °C | - | - |  | 1oo1 | Rectifier Cooling Outlet - Temperature High |  | 25.04.2025 no change | F.Reinhart | V3.0, BM, 7.11.2023: new modular rectifier design; 48°C is equal to the rectifier inlet temperature during type test
|  | A | 3.3 |  |  | AL 3.0 | - | 2.0 | °C | - | - | - | 1oo1 | Rectifier Cooling Outlet - Temperature Low | Freeze Warning Rectifier Cooling | 25.04.2025 implemented change | F. Reinhart | V3.3, JS, BM, 6.11.2024: freeze protection is also covered by low flow trip. therefore this cause&effect was shifted from protection by BT01 to warnings of BQ01 only
#REF! |  | A | 1.4 | G01NHA01KF001-BAxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Voltage monitoring - Rectifier cabinet 1 | Fuse trip | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.4 | G01NHA01KF001-FCxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Voltage monitoring/distribution - Rectifier cabinet 1 | Fuse trip | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.4 | G01NHA01KF001-QAxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Voltage distribution - Rectifier cabinet 1 | Fuse trip | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.4 | G01NHA01KF001-TBxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | UPS Generation - Rectifier cabinet 1 | Fuse trip | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.4 | G01NHA01KF002-BAxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Voltage monitoring - Rectifier cabinet 2 | Fuse trip | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.4 | G01NHA01KF002-FCxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Voltage monitoring/distribution - Rectifier cabinet 2 | Fuse trip | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.4 | G01NHA01KF002-QAxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Voltage distribution - Rectifier cabinet 2 | Fuse trip | 25.04.2025 no change | F.Reinhart
#REF! |  | A | 1.4 | G01NHA01KF002-TBxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | UPS Generation - Rectifier cabinet 2 | Fuse trip | 25.04.2025 no change | F.Reinhart
|  | A | 1.4 | G01NHA01BZ001-FC01 | XU01 | 0 |  |  | BOOL |  |  |  | 1oo1 | 24VDC Distribution fault - Rectifier 1 | Group fault alarm | 25.04.2025 no change | F.Reinhart
|  | A | 1.4 | G01NHA01BZ002-FC01 | XU01 | 0 |  |  | BOOL |  |  |  | 1oo1 | 24VDC Distribution fault - Rectifier 2 | Group fault alarm | 25.04.2025 no change | F.Reinhart
|  | A | 1.4 | G01NHA01BZ003-FC01 | XU01 | 0 |  |  | BOOL |  |  |  | 1oo1 | 24VDC Distribution fault - Rectifier 3 | Group fault alarm | 25.04.2025 no change | F.Reinhart
|  | A | 1.4 | G01NHA01BZ004-FC01 | XU01 | 0 |  |  | BOOL |  |  |  | 1oo1 | 24VDC Distribution fault - Rectifier 4 | Group fault alarm | 25.04.2025 no change | F.Reinhart
|  | A | 1.4 | G01NHA01BZ001-TF01 | XW01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Isolation warning - Rectifier 1 | Group warning of isolation monitoring | 25.04.2025 no change | F.Reinhart | V1.4 (FR): added message
|  | A | 1.4 | G01NHA01BZ002-TF01 | XW01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Isolation warning - Rectifier 2 | Group warning of isolation monitoring | 25.04.2025 no change | F.Reinhart | V1.4 (FR): added message
|  | A | 1.4 | G01NHA01BZ003-TF01 | XW01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Isolation warning - Rectifier 3 | Group warning of isolation monitoring | 25.04.2025 no change | F.Reinhart | V1.4 (FR): added message
|  | A | 1.4 | G01NHA01BZ004-TF01 | XW01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Isolation warning - Rectifier 4 | Group warning of isolation monitoring | 25.04.2025 no change | F.Reinhart | V1.4 (FR): added message
|  | A | 1.4 | G01NHA01QZ001-QB11 | XB02 | 0 |  |  | BOOL |  |  |  | 1oo1 | Main switch - Disconnector DC+ Rectifier 1 | Check back off | 25.04.2025 no change | F.Reinhart
|  | A | 1.4 | G01NHA01QZ001-QB12 | XB02 | 0 |  |  | BOOL |  |  |  | 1oo1 | Main switch - Disconnector DC- Rectifier 1 | Check back off | 25.04.2025 no change | F.Reinhart
|  | A | 1.4 | G01NHA01QZ002-QB11 | XB02 | 0 |  |  | BOOL |  |  |  | 1oo1 | Main switch - Disconnector DC+ Rectifier 2 | Check back off | 25.04.2025 no change | F.Reinhart
|  | A | 1.4 | G01NHA01QZ002-QB12 | XB02 | 0 |  |  | BOOL |  |  |  | 1oo1 | Main switch - Disconnector DC- Rectifier 2 | Check back off | 25.04.2025 no change | F.Reinhart
|  | A | 1.4 | G01NHA01QZ003-QB11 | XB02 | 0 |  |  | BOOL |  |  |  | 1oo1 | Main switch - Disconnector DC+ Rectifier 3 | Check back off | 25.04.2025 no change | F.Reinhart
|  | A | 1.4 | G01NHA01QZ003-QB12 | XB02 | 0 |  |  | BOOL |  |  |  | 1oo1 | Main switch - Disconnector DC- Rectifier 3 | Check back off | 25.04.2025 no change | F.Reinhart
|  | A | 1.4 | G01NHA01QZ004-QB11 | XB02 | 0 |  |  | BOOL |  |  |  | 1oo1 | Main switch - Disconnector DC+ Rectifier 4 | Check back off | 25.04.2025 no change | F.Reinhart
|  | A | 1.4 | G01NHA01QZ004-QB12 | XB02 | 0 |  |  | BOOL |  |  |  | 1oo1 | Main switch - Disconnector DC- Rectifier 4 | Check back off | 25.04.2025 no change | F.Reinhart
|  | A | 3.3 | G01NHA01EQ001-QN02 | XU01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Control Valve - Rectifier Cooling Unit Cooling Water | Group fault alarm | 25.04.2025 implemented change | F. Reinhart | V3.2, BM, 03.11.2023: new valve V3.3, KB, 16.07.2023: Group warning active on "0"
To Balance of Plant
Move to messages |  | A |  | G01NHC01HP001-BP02 | XQ01 |  |  |  | bar(g) |  |  |  | 1oo1 |  | Pressure Sensor 2 - H2 Header (-25 to 225 mbarg) via hardwire |  |  |  | H2 Header Pressure (For information only)
Note:
|  | 1 |  | There is no specific constant pressure piston buffer tank in H2 Sakura project downstream of product control valve. Hence customer's contant volume tank to be reffered as buffer tank/volume
|  | 2 |  | The cause-and-effect relationships outlined herein are provided solely on the basis of Siemens Energy’s limited experience with complete plant configurations. They are intended for preliminary guidance only and shall not be construed as comprehensive, exhaustive, or finalized from Siemens Energy’s side.
The Customer shall bear full responsibility for conducting detailed investigations, including but not limited to project-specific HAZOP and HAZID studies, to identify any critical causes at the complete plant level that may trigger array safety-related effects.
Any additional causes or effects identified by the Customer may be proposed for inclusion. Incorporation into the safety matrix and associated logic shall be subject to mutual agreement between Siemens Energy and the Customer.
Transformer (IGBT) | Transformer (IGBT)
Transformer (IGBT) |  |  | 3.3 | G01NHA01TA001-BU01 | XM01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Buchholzrelay AL1
Transformer (IGBT) |  |  | 3.3 | G01NHA01TA001-BT01 | XM01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Oil Temp. Transformer Alarm 1
#REF! |  |  | 3.3 | G01NHA01TA001-BT02 | XM01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Winding Temperature Transformer Al1
#REF! |  |  | 3.3 | G01NHA01TA001-BL01 | XM01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Oil Level Min
#REF! |  |  | 3.3 | G01NHA01TA001-BL01 | XM02 | 0 | - | - | BOOL | - | - |  | 1oo1 | Oil Level Max
#REF! |  |  | 3.3 | G01NHA01TA001-BL03 | XM01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Tap changer oil Level Min
#REF! |  |  | 3.3 | G01NHA01TA001-BL03 | XM02 | 0 | - | - | BOOL | - | - |  | 1oo1 | Tap changer oil Level Max
#REF! |  |  | 3.3 | G01NHA01TA001-QA02 | XR01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Tap changer not running | Feedback - Main Circuit Breaker ON
#REF! |  |  | 3.3 | G01NHA01TA001-QA02 | XV01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Tap changer invalid position
#REF! |  |  | 3.3 | G01NHA01TA001-QA02 | XB07 | 0 | - | - | BOOL | - | - |  | 1oo1 | Tap changer - not Remote
#REF! |  |  | 3.3 | G01NHA01TA002-BU01 | XM01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Buchholzrelay AL1
#REF! |  |  | 3.3 | G01NHA01TA002-BT01 | XM01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Oil Temp. Transformer Alarm 1
#REF! |  |  | 3.3 | G01NHA01TA002-BT02 | XM01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Winding Temperature Transformer Al1
#REF! |  |  | 3.3 | G01NHA01TA002-BL01 | XM01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Oil Level Min
#REF! |  |  | 3.3 | G01NHA01TA002-BL01 | XM02 | 0 | - | - | BOOL | - | - |  | 1oo1 | Oil Level Max
#REF! |  |  | 3.3 | G01NHA01TA002-BL03 | XM01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Tap changer oil Level Min
#REF! |  |  | 3.3 | G01NHA01TA002-BL03 | XM02 | 0 | - | - | BOOL | - | - |  | 1oo1 | Tap changer oil Level Max
#REF! |  |  | 3.3 | G01NHA01TA002-QA02 | XR01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Tap changer not running | Feedback - Main Circuit Breaker ON
#REF! |  |  | 3.3 | G01NHA01TA002-QA02 | XV01 | 0 | - | - | BOOL | - | - |  | 1oo1 | Tap changer invalid position
#REF! |  |  | 3.3 | G01NHA01TA002-QA02 | XB07 | 0 | - | - | BOOL | - | - |  | 1oo1 | Tap changer - not Remote
|  |  | 3.3 | G01NHA01TA001-FCxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Voltage distribution - Transformer panel | Fuse trip
Rectifier IGBT (Optional) | Rectifier IGBT (Optional)
#REF! |  |  | 3.3 | G01NHA01KF001-BAxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Voltage monitoring - I&C Rectifier cabinet | Abnormal voltage
#REF! |  |  | 3.3 | G01NHA01KF001-FCxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Voltage monitoring/distribution - I&C Rectifier cabinet | Fuse trip
#REF! |  |  | 3.3 | G01NHA01KF001-QAxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Voltage distribution - I&C Rectifier cabinet | Fuse trip
#REF! |  |  | 3.3 | G01NHA01KF001-TBxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | 24 VDC Generation - I&C Rectifier cabinet | Group fault alarm
#REF! |  |  | 3.3 | G01NHA01TB001-KFxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Voltage distribution, UPS - Converter controller Row 1 | Fuse trip
#REF! |  |  | 3.3 | G01NHA01TB001-TAxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | 24 VDC Generation - Converter controller Row 1 | Group fault alarm
#REF! |  |  | 3.3 | G01NHA01TB002-KFxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Voltage distribution, UPS - Converter controller Row 1 | Fuse trip
#REF! |  |  | 3.3 | G01NHA01TB002-TAxx | XB01 | 0 |  |  | BOOL |  |  |  | 1oo1 | 24 VDC Generation - Converter controller Row 1 | Group fault alarm
|  |  | 3.3 | G01NHA01BZ011-TF01 | XW01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Isolation warning - Electrolyzer Row 1 | Group warning of isolation monitoring
|  |  | 3.3 | G01NHA01BZ012-TF01 | XW01 | 0 |  |  | BOOL |  |  |  | 1oo1 | Isolation warning - Electrolyzer Row 2 | Group warning of isolation monitoring
|  |  | 3.3 | G01NHA01QZ001-QA10 | XB02 | 0 |  |  | BOOL |  |  |  | 1oo1 | LV AC CB of converter system 1 Row 1 OFF (open) | Check back off
|  |  | 3.3 | G01NHA01QZ001-QA20 | XB02 | 0 |  |  | BOOL |  |  |  | 1oo1 | LV AC CB of converter system 2 Row 1 OFF (open) | Check back off
|  |  | 3.3 | G01NHA01QZ001-QA30 | XB02 | 0 |  |  | BOOL |  |  |  | 1oo1 | LV AC CB of converter system 3 Row 1 OFF (open) | Check back off
|  |  | 3.3 | G01NHA01QZ001-QA40 | XB02 | 0 |  |  | BOOL |  |  |  | 1oo1 | LV AC CB of converter system 4 Row 1 OFF (open) | Check back off
|  |  | 3.3 | G01NHA01QZ001-QA12 | XB02 | 0 |  |  | BOOL |  |  |  | 1oo1 | LV DC of converter system 1/2 Row 1 OFF (open) | Check back off
|  |  | 3.3 | G01NHA01QZ001-QA32 | XB02 | 0 |  |  | BOOL |  |  |  | 1oo1 | LV DC of converter system 3/4 Row 1 OFF (open) | Check back off
|  |  | 3.3 | G01NHA01QZ002-QA10 | XB02 | 0 |  |  | BOOL |  |  |  | 1oo1 | LV AC CB of converter system 1 Row 2 OFF (open) | Check back off
|  |  | 3.3 | G01NHA01QZ002-QA20 | XB02 | 0 |  |  | BOOL |  |  |  | 1oo1 | LV AC CB of converter system 2 Row 2 OFF (open) | Check back off
|  |  | 3.3 | G01NHA01QZ002-QA30 | XB02 | 0 |  |  | BOOL |  |  |  | 1oo1 | LV AC CB of converter system 3 Row 2 OFF (open) | Check back off
|  |  | 3.3 | G01NHA01QZ002-QA40 | XB02 | 0 |  |  | BOOL |  |  |  | 1oo1 | LV AC CB of converter system 4 Row 2 OFF (open) | Check back off
|  |  | 3.3 | G01NHA01QZ002-QA12 | XB02 | 0 |  |  | BOOL |  |  |  | 1oo1 | LV DC of converter system 1/2 Row 2 OFF (open) | Check back off
|  |  | 3.3 | G01NHA01QZ002-QA32 | XB02 | 0 |  |  | BOOL |  |  |  | 1oo1 | LV DC of converter system 3/4 Row 2 OFF (open) | Check back off
Note on B62: Mahor, Abhishek (ext): Check with V3.4, With Bernd
Note on B120: Mahor, Abhishek (ext): Check with V 3.4

## var. level limits (intern)
Variable limits for level NHC/E01BL001-BL01 & BL02
*Reference current measurement (SIL): sum of =G01NHA01BZ011/012/013/014-BC01
**Reference current measurement: sum of =G01NHA01TB001/002/003/004-KZ75 (in case of communication fault to rectifier use SIL measurement as substitution value)
|  |  | BL01 | BL02 | BL02 | BL01&BL02 | BL02
|  | Load* | SIS trip* | oper. Trip** | warning** | Delay coming | op. set point**
|  | 0 | 5 | 12.2 | 13.2 | 3 min | 20
|  | 6000 | 10.3 | 12.3 | 13.3 |  | 22
|  | 12000 | 13.7 | 15.7 | 16.7 |  | 24
|  | 20000 | 17.5 | 19.5 | 20.5 |  | 26.6667
|  | 26000 | 19.4 | 21.4 | 22.4 |  | 28.6667
|  | 30000 | 20.4 | 22.4 | 23.4 |  | 30
| overload case | 31200 | 20.7 | 22.7 | 23.7 |  | 30.4
- INTERNAL -

## Remarks & Abbreviations
General Remarks
Warning is without A_DC (Delay Coming) except for warning only
Boolean type is defined to be active "1" if within range/valid/OK, thus fault/warning/alarm signals become "0" when not OK; Otherwise broken cable would remain undetected
Detected fault of a signal shall have same effect as exceeding limit value (exceptions marked in comments of cause)
Action defines state that shall be achieved
Output Tag and Value are chosen based on available signals to achieve required action. E.g. on may be "not off" or "on" signal type and value
Warning Level does not cause action and is issued immediate except A_DC/A_DG is defined without Alarm/Limit
Alarm/Limit with A_DC/A_DG is relevant for listed action
S* actions are not required to achieve safe state as part of SIF, but are initiated in parallel i.e. without SIL-rating, but connected via failsafe I/O
no inertization/no purge required can only be reset automatically upon positive inertization/purge proof (sufficient purge volume and flow)
actions with feedback not listed in safety matrix do not cause action, only warning is generated
all mentioned hardware signals should cause an alarm on the switch/safety limit; when several signals are required together to trigger a cause (e.g. 2oo2), there must be an extra alarm message for the cause
all actuators generate a control signal fault on control error (e.g. feedback does not match control after monitoring time)
Maintenance Override (MOS) of SIS functions is by default only enabled, when key switch protection is inactive (any other condition for safe state is mentioned in the comments)
Color Coding:
fail safe signal processing
non-fail safe signal processing
changed in latest revision
Abbreviations
? | tbd/project specific
A_DC | alarm delay coming
A_DG | alarm delay going
AC | Alternating Current
AL | alarm
BOOL | boolean
CB | Circuit Breaker
Chgd | document version introducing latest change
DCC | document classification code
Delta | deviation monitoring function
Demin | demineralized/demineralization
diff | difference
discont | discontinuously
ESD | emergency shutdown
Func | Function or fault tolerance
H2 | Hydrogen
HX | heat exchanger
Hyst | hysteresis
max | maximum
min | minimum
MV | medium voltage
N2 | Nitrogen
O2 | Oxygen
PCV | product control valve
PLS# | identifier of operational shutoff function (if assigned)
PolRect | polarization rectifier
Rect | rectifier
SIF | Safety Instrumented Function
SIL | Safety Integrity Level
SIS# | Safety Instrumented System identifier of safety instrumented function (SIF) acc. to safety requirement specification (SRS)
SLC | subloop control
stby | standby
STO | Safe Torque Off, hardwired fast rectifier (SINAMICS DCM) OFF command for functional safety purposes
tbd | to be determined
Temp | temperature
UPS | uninerruptible power supply
Warn | warning
YooX | Yth fault out of X signals causes action. (if X or Y is actually listed the amount: tbd/project specific)

## Query (hidden)
Unit | Device | Symbol address | Short full |  | Long Full | Mainsystem | Mainsystem - Description | Main System Number | Mainsystem Number - Description | System | System - Description | System Number | System Number - Description | Base Function | Base Function - Description | Base Function Number | Base Function Number - Description | Device | Device description | Signal tag | Signal description | Mainsystem Number - Short | System Number - Short | Base Function Number - Short | Device - Short | Signal description - Short | Sensor/Device | Signal type - HW | Signal level - HW | Signal level - HW | Connection type - HW | Signal form - HW | invChannelRequest | Data type | Signal type - CH | Failsafe - CH | Function | Meas. range Min | Meas. range Max | Display range Min | Display range MAX | Unit | .HH | Limit value | .H | Limit value | .L | Limit value | .LL | Limit value | Safety relevant | SIL class | IED | IED type | TerminalFrom | ConFrom | invIO | Loop doc number | P&ID doc number | Revision status | Revision comment |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-BF01 | =G01NHC01BQ001-BF01;XG02 | ELY1 H2 TRT QUAL FLOW1 CB ON/OPN/MIN1 | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM 10301; FLOWMETER GENERAL CHECK BACK OFF/CLOSED // LIMIT VALUE >MIN 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -BF01 | 10301; Flowmeter general | XG02 | Check back off/closed // Limit value >min 1 | Ely1 | H2 TRT | QUAL | Flow1 | CB ON/OPN/MIN1 | -BF01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | FSZ | [7 empty] | AH |  | AL |  |  |  | Yes |  | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:1 | 1B | 01 | =G01NHC01BQ001-BF01&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100 | 0
=A01GCF01CM001 | A01GCF01CM001-BL01 | =A01GCF01CM001-BL01;XQ01 | AUX DEMIN SUP TNK1 LVL1 ANALOG1 | 31 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS DEMIN WATER SUPPLY SYSTEM DEMIN WATER SUPPLY SYSTEM 1 BUFFER TANK BUFFER TANK 1 LEVEL - BUFFER TANK ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | GCF | Demin Water Supply System | 01 | Demin Water Supply System 1 | CM | Buffer Tank | 001 | Buffer Tank 1 | -BL01 | Level - Buffer Tank | XQ01 | Analog process signal | Aux | Demin Sup | Tnk1 | Lvl1 | ANALOG1 | DR | Electrical | 4..20 mA | 4..20 mA | Field bus | Continuous signal |  |  | AI | 0 | LIC | [7 empty] | AH |  | AL |  | ASLL | [9 empty] | =A01GCF01&MFB.001
=A01GCF01GP001 | A01GCF01GP001-BP01 | =A01GCF01GP001-BP01;XQ01 | AUX DEMIN SUP PMP1 PRES1 ANALOG1 | 32 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS DEMIN WATER SUPPLY SYSTEM DEMIN WATER SUPPLY SYSTEM 1 PUMP SYSTEM PUMP SYSTEM 1 PRESSURE - DEMIN WATER OUTLET ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | GCF | Demin Water Supply System | 01 | Demin Water Supply System 1 | GP | Pump System | 001 | Pump System 1 | -BP01 | Pressure - Demin Water Outlet | XQ01 | Analog process signal | Aux | Demin Sup | PMP1 | Pres1 | ANALOG1 | DR | Electrical | 4..20 mA | 4..20 mA | Field bus | Continuous signal |  |  | AI | 0 | PI | [7 empty] | AH |  | AL | [11 empty] | =A01GCF01&MFB.001 |  |  |  | U012UBB01UC001
=A01GCF01GP001 | A01GCF01GP001-BQ01 | =A01GCF01GP001-BQ01;XQ01 | AUX DEMIN SUP PMP1 QUAL1 ANALOG1 | 32 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS DEMIN WATER SUPPLY SYSTEM DEMIN WATER SUPPLY SYSTEM 1 PUMP SYSTEM PUMP SYSTEM 1 CONDUCTIVITY - DEMIN WATER OUTLET ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | GCF | Demin Water Supply System | 01 | Demin Water Supply System 1 | GP | Pump System | 001 | Pump System 1 | -BQ01 | Conductivity - Demin Water Outlet | XQ01 | Analog process signal | Aux | Demin Sup | PMP1 | Qual1 | ANALOG1 | DR | Electrical | 4..20 mA | 4..20 mA | Field bus | Continuous signal |  |  | AI | 0 | AI | [7 empty] | AH | [13 empty] | =A01GCF01&MFB.001 |  |  |  | U012UNA01UH111
=A01GCF01HN001 | A01GCF01HN001-BF01 | =A01GCF01HN001-BF01;XQ01 | AUX DEMIN SUP PROD U1 FLOW1 ANALOG1 | 35 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS DEMIN WATER SUPPLY SYSTEM DEMIN WATER SUPPLY SYSTEM 1 PRODUCTION UNIT PRODUCTION UNIT 1 FLOWMETER - WATER INLET ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | GCF | Demin Water Supply System | 01 | Demin Water Supply System 1 | HN | Production Unit | 001 | Production Unit 1 | -BF01 | Flowmeter - Water Inlet | XQ01 | Analog process signal | Aux | Demin Sup | PROD U1 | Flow1 | ANALOG1 | -BF01 | Electrical | 4..20 mA | 4..20 mA | Field bus | Continuous signal |  |  | AI | 0 | FI | [21 empty] | =A01GCF01&MFB.001 |  |  |  | U012UNA01UH112
=A01GCF01HN001 | A01GCF01HN001-BP01 | =A01GCF01HN001-BP01;XQ01 | AUX DEMIN SUP PROD U1 PRES1 ANALOG1 | 35 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS DEMIN WATER SUPPLY SYSTEM DEMIN WATER SUPPLY SYSTEM 1 PRODUCTION UNIT PRODUCTION UNIT 1 PRESSURE - WATER INLET ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | GCF | Demin Water Supply System | 01 | Demin Water Supply System 1 | HN | Production Unit | 001 | Production Unit 1 | -BP01 | Pressure - Water Inlet | XQ01 | Analog process signal | Aux | Demin Sup | PROD U1 | Pres1 | ANALOG1 | -BP01 | Electrical | 4..20 mA | 4..20 mA | Field bus | Continuous signal |  |  | AI | 0 | PI | [21 empty] | =A01GCF01&MFB.001 |  |  |  | U012UNA01UH121
=A01GCF01HN001 | A01GCF01HN001-BQ01 | =A01GCF01HN001-BQ01;XQ01 | AUX DEMIN SUP PROD U1 QUAL1 ANALOG1 | 35 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS DEMIN WATER SUPPLY SYSTEM DEMIN WATER SUPPLY SYSTEM 1 PRODUCTION UNIT PRODUCTION UNIT 1 CONDUCTIVITY - WATER INLET ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | GCF | Demin Water Supply System | 01 | Demin Water Supply System 1 | HN | Production Unit | 001 | Production Unit 1 | -BQ01 | Conductivity - Water Inlet | XQ01 | Analog process signal | Aux | Demin Sup | PROD U1 | Qual1 | ANALOG1 | -BQ01 | Electrical | 4..20 mA | 4..20 mA | Field bus | Continuous signal |  |  | AI | 0 | AI | 0 µS/cm | 20 µS/cm | [19 empty] | =A01GCF01&MFB.001 |  |  |  | U012UNA01UH122
=A01GCF01HN001 | A01GCF01HN001-BQ01 | =A01GCF01HN001-BQ01;XQ02 | AUX DEMIN SUP PROD U1 QUAL1 ANALOG2 | 35 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS DEMIN WATER SUPPLY SYSTEM DEMIN WATER SUPPLY SYSTEM 1 PRODUCTION UNIT PRODUCTION UNIT 1 CONDUCTIVITY - WATER INLET ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | GCF | Demin Water Supply System | 01 | Demin Water Supply System 1 | HN | Production Unit | 001 | Production Unit 1 | -BQ01 | Conductivity - Water Inlet | XQ02 | Analog process signal | Aux | Demin Sup | PROD U1 | Qual1 | ANALOG2 | -BQ01 | Electrical | 4..20 mA | 4..20 mA | Field bus | Continuous signal |  |  | AI | 0 | TI | 0 µS/cm | 20 µS/cm | [19 empty] | =A01GCF01&MFB.001 |  |  |  | U012UNA01UH131
=A01PAD01EZ001 | A01PAD01EZ001-BT01 | =A01PAD01EZ001-BT01;XQ01 | AUX COOL WTR RECOOL TEMP1 ANALOG1 | 33 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING SYSTEMS RECOOLING CIRCUIT TEMPERATURE - COOLER SYSTEM OUTLET ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | EZ | Recooling Systems | 001 | Recooling Circuit | -BT01 | Temperature - Cooler System Outlet | XQ01 | Analog process signal | Aux | Cool Wtr | ReCool | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Field bus | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 80 °C | [5 empty] | AH | [13 empty] | =A01PAD01&MFB.001 |  |  |  | U012UNA01UH132
=A01PAD01EZ001 | A01PAD01EZ001-EQ01GQ01 | PAD01EZ001-EQ01GQ01;XQ01 | AUX COOL WTR RECOOL AIR1-1 ANALOG1 | 34 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING SYSTEMS RECOOLING CIRCUIT AIR COOLED HEAT EXCHANGER 1 - 1 ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | EZ | Recooling Systems | 001 | Recooling Circuit | -EQ01GQ01 | Air Cooled Heat Exchanger 1 - 1 | XQ01 | Analog process signal | Aux | Cool Wtr | ReCool | Air1-1 | ANALOG1 |  | Electrical | Undefined | Undefined | Field bus | Continuous signal |  |  | AI | 0 | NS | [21 empty] | =A01PAD01&MFB.001 |  |  |  | U012UNA01UH141
=A01PAD01EZ001 | A01PAD01EZ001-EQ01GQxx | PAD01EZ001-EQ01GQxx;XQ01 | AUX COOL WTR RECOOL AIR1-X ANALOG1 | 34 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING SYSTEMS RECOOLING CIRCUIT AIR COOLED HEAT EXCHANGER 1 - X ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | EZ | Recooling Systems | 001 | Recooling Circuit | -EQ01GQxx | Air Cooled Heat Exchanger 1 - x | XQ01 | Analog process signal | Aux | Cool Wtr | ReCool | Air1-x | ANALOG1 |  | Electrical | Undefined | Undefined | Field bus | Continuous signal |  |  | AI | 0 | NS | [21 empty] | =A01PAD01&MFB.001 |  |  |  | U012UNA01UH142
=A01PAD01EZ001 | A01PAD01EZ001-EQ02GQ01 | PAD01EZ001-EQ02GQ01;XQ01 | AUX COOL WTR RECOOL AIR2-1 ANALOG1 | 34 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING SYSTEMS RECOOLING CIRCUIT AIR COOLED HEAT EXCHANGER 2 - 1 ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | EZ | Recooling Systems | 001 | Recooling Circuit | -EQ02GQ01 | Air Cooled Heat Exchanger 2 - 1 | XQ01 | Analog process signal | Aux | Cool Wtr | ReCool | Air2-1 | ANALOG1 |  | Electrical | Undefined | Undefined | Field bus | Continuous signal |  |  | AI | 0 | NS | [21 empty] | =A01PAD01&MFB.001 |  |  |  | U012UNA01UH151
=A01PAD01EZ001 | A01PAD01EZ001-EQ02GQxx | PAD01EZ001-EQ02GQxx;XQ01 | AUX COOL WTR RECOOL AIR2-X ANALOG1 | 34 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING SYSTEMS RECOOLING CIRCUIT AIR COOLED HEAT EXCHANGER 2 - X ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | EZ | Recooling Systems | 001 | Recooling Circuit | -EQ02GQxx | Air Cooled Heat Exchanger 2 - x | XQ01 | Analog process signal | Aux | Cool Wtr | ReCool | Air2-x | ANALOG1 |  | Electrical | Undefined | Undefined | Field bus | Continuous signal |  |  | AI | 0 | NS | [21 empty] | =A01PAD01&MFB.001 |  |  |  | U012UNA01UH152
=A01PAD01EZ001 | A01PAD01EZ001-EQ03GQ01 | PAD01EZ001-EQ03GQ01;XQ01 | AUX COOL WTR RECOOL AIR3-1 ANALOG1 | 34 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING SYSTEMS RECOOLING CIRCUIT AIR COOLED HEAT EXCHANGER 3 - 1 ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | EZ | Recooling Systems | 001 | Recooling Circuit | -EQ03GQ01 | Air Cooled Heat Exchanger 3 - 1 | XQ01 | Analog process signal | Aux | Cool Wtr | ReCool | Air3-1 | ANALOG1 |  | Electrical | Undefined | Undefined | Field bus | Continuous signal |  |  | AI | 0 | NS | [21 empty] | =A01PAD01&MFB.001 |  |  |  | U012UNA01UH161
=A01PAD01EZ001 | A01PAD01EZ001-EQ03GQxx | PAD01EZ001-EQ03GQxx;XQ01 | AUX COOL WTR RECOOL AIR3-X ANALOG1 | 34 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING SYSTEMS RECOOLING CIRCUIT AIR COOLED HEAT EXCHANGER 3 - X ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | EZ | Recooling Systems | 001 | Recooling Circuit | -EQ03GQxx | Air Cooled Heat Exchanger 3 - x | XQ01 | Analog process signal | Aux | Cool Wtr | ReCool | Air3-x | ANALOG1 |  | Electrical | Undefined | Undefined | Field bus | Continuous signal |  |  | AI | 0 | NS | [21 empty] | =A01PAD01&MFB.001 |  |  |  | U012UNA01UH162
=A01PAD01GP001 | A01PAD01GP001-BP01 | =A01PAD01GP001-BP01;XQ01 | AUX COOL WTR PMP1 PRES1 ANALOG1 | 31 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING PUMP SYSTEM RECOOLING PUMP UNIT DIFF.-PRESSURE - COOLING PUMP 1 ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | GP | Recooling Pump System | 001 | Recooling Pump Unit | -BP01 | Diff.-Pressure - Cooling Pump 1 | XQ01 | Analog process signal | Aux | Cool Wtr | PMP1 | Pres1 | ANALOG1 | -BP01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | PD | [5 empty] | ASHH |  | AH | [13 empty] | =A01PAD01&MFB.001 |  |  |  | U012UBB01UC002
=A01PAD01GP001 | A01PAD01GP001-BP02 | =A01PAD01GP001-BP02;XQ01 | AUX COOL WTR PMP1 PRES2 ANALOG1 | 31 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING PUMP SYSTEM RECOOLING PUMP UNIT DIFF.-PRESSURE - COOLING PUMP 2 ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | GP | Recooling Pump System | 001 | Recooling Pump Unit | -BP02 | Diff.-Pressure - Cooling Pump 2 | XQ01 | Analog process signal | Aux | Cool Wtr | PMP1 | Pres2 | ANALOG1 | -BP02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | PD | [5 empty] | ASHH |  | AH | [13 empty] | =A01PAD01&MFB.001 |  |  |  | U012UBB01UH001
=A01PAD01GP001 | A01PAD01GP001-BP03 | =A01PAD01GP001-BP03;XQ01 | AUX COOL WTR PMP1 PRES3 ANALOG1 | 31 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING PUMP SYSTEM RECOOLING PUMP UNIT PRESSURE - COOLING PUMP INPUT ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | GP | Recooling Pump System | 001 | Recooling Pump Unit | -BP03 | Pressure - Cooling Pump Input | XQ01 | Analog process signal | Aux | Cool Wtr | PMP1 | Pres3 | ANALOG1 | -BP03 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | PI | 0 bar | 8 bar |  |  |  | ASHH |  | AH |  | AL |  | ASLL | [9 empty] | =A01PAD01&MFB.001 |  |  |  | U012UBB01UH002
=A01PAD01GP001 | A01PAD01GP001-BT01 | =A01PAD01GP001-BT01;XQ01 | AUX COOL WTR PMP1 TEMP1 ANALOG1 | 31 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING PUMP SYSTEM RECOOLING PUMP UNIT TEMPERATURE - COOLING PUMP INPUT ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | GP | Recooling Pump System | 001 | Recooling Pump Unit | -BT01 | Temperature - Cooling Pump Input | XQ01 | Analog process signal | Aux | Cool Wtr | PMP1 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | -20 °C | 80 °C | [19 empty] | =A01PAD01&MFB.001
=A01PAD01KF001 | A01PAD01KF001-BT01 | =A01PAD01KF001-BT01;XQ01 | AUX COOL WTR CTRL U1 TEMP1 ANALOG1 | 34 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM CONTROL UNIT SYSTEM COOLING WATER SYSTEM CONTROL UNIT TEMPERATURE - OUTSIDE ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | KF | Control Unit System | 001 | Cooling Water System Control Unit | -BT01 | Temperature - Outside | XQ01 | Analog process signal | Aux | Cool Wtr | CTRL U1 | Temp1 | ANALOG1 | DR | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | -40 °C | 60 °C | [19 empty] | =K01&MFB.001
=A01PAD01WP001 | A01PAD01WP001-BF01 | =A01PAD01WP001-BF01;XQ01 | AUX COOL WTR PIPING FLOW1 ANALOG1 | 33 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING WATER DISTRIBUTION SYSTEM COOLING WATER PIPE SYSTEM FLOWMETER - COOLING SYSTEM OUTLET ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | WP | Recooling Water Distribution System | 001 | Cooling Water Pipe System | -BF01 | Flowmeter - Cooling System Outlet | XQ01 | Analog process signal | Aux | Cool Wtr | Piping | Flow1 | ANALOG1 | -BF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | FI | [21 empty] | =A01PAD01&MFB.001
=A01PAD01WP001 | A01PAD01WP001-BP01 | =A01PAD01WP001-BP01;XQ01 | AUX COOL WTR PIPING PRES1 ANALOG1 | 33 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING WATER DISTRIBUTION SYSTEM COOLING WATER PIPE SYSTEM PRESSURE - COOLING SYSTEM OUTLET ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | WP | Recooling Water Distribution System | 001 | Cooling Water Pipe System | -BP01 | Pressure - Cooling System Outlet | XQ01 | Analog process signal | Aux | Cool Wtr | Piping | Pres1 | ANALOG1 | -BP01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | PI | 0 bar | 8 bar | [5 empty] | AH | [13 empty] | =A01PAD01&MFB.001
=A01PAD01WP001 | A01PAD01WP001-BT01 | =A01PAD01WP001-BT01;XQ01 | AUX COOL WTR PIPING TEMP1 ANALOG1 | 33 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING WATER DISTRIBUTION SYSTEM COOLING WATER PIPE SYSTEM TEMPERATURE - COOLING SYSTEM OUTLET ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | WP | Recooling Water Distribution System | 001 | Cooling Water Pipe System | -BT01 | Temperature - Cooling System Outlet | XQ01 | Analog process signal | Aux | Cool Wtr | Piping | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | -20 °C | 80 °C | [5 empty] | AH |  | AL |  | ASLL | [9 empty] | =A01PAD01&MFB.001
=A01PAD01WP001 | A01PAD01WP001-BT02 | =A01PAD01WP001-BT02;XQ01 | AUX COOL WTR PIPING TEMP2 ANALOG1 | 33 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING WATER DISTRIBUTION SYSTEM COOLING WATER PIPE SYSTEM TEMPERATURE - COMPRESSOR COOLINGWATER RETURN ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | WP | Recooling Water Distribution System | 001 | Cooling Water Pipe System | -BT02 | Temperature - Compressor Coolingwater Return | XQ01 | Analog process signal | Aux | Cool Wtr | Piping | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | -20 °C | 80 °C | [19 empty] | =A01PAD01&MFB.002
=A01PAD01WP001 | A01PAD01WP001-BT03 | =A01PAD01WP001-BT03;XQ01 | AUX COOL WTR PIPING TEMP3 ANALOG1 | 33 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING WATER DISTRIBUTION SYSTEM COOLING WATER PIPE SYSTEM TEMPERATURE - HVAC COOLINGWATER RETURN ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | WP | Recooling Water Distribution System | 001 | Cooling Water Pipe System | -BT03 | Temperature - HVAC Coolingwater Return | XQ01 | Analog process signal | Aux | Cool Wtr | Piping | Temp3 | ANALOG1 | -BT03 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | -20 °C | 80 °C | [19 empty] | =A01PAD01&MFB.002
=A01PAD01WP001 | A01PAD01WP001-QN01 | =A01PAD01WP001-QN01;XQ01 | AUX COOL WTR PIPING CV1 ANALOG1 | 31 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING WATER DISTRIBUTION SYSTEM COOLING WATER PIPE SYSTEM CONTROL VALVE - COMPRESSOR COOLINGWATER RETURN ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | WP | Recooling Water Distribution System | 001 | Cooling Water Pipe System | -QN01 | Control valve - Compressor Coolingwater Return | XQ01 | Analog process signal | Aux | Cool Wtr | Piping | CV1 | ANALOG1 | DR | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | G | [17 empty] | B10:XQ01 | EA01 |  |  | =A01PAD01&MFB.002
=A01QFB01QM001 | A01QFB01QM001-BP01 | =A01QFB01QM001-BP01;XQ01 | AUX CTRL AIR DIST PRES1 ANALOG1 | 31 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS INSTRUMENT AIR SUPPLY SYSTEM INSTRUMENT AIR SUPPLY SYSTEM 1 INSTRUMENT AIR DISTRIBUTION SYSTEM INSTRUMENT AIR DISTRIBUTION 10922; GAUGE PRESSURE TRANSM. WITHOUT PRESSURE REPEATER ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | QFB | Instrument Air Supply System | 01 | Instrument Air Supply System 1 | QM | Instrument Air Distribution System | 001 | Instrument Air Distribution | -BP01 | 10922; Gauge pressure transm. without pressure repeater | XQ01 | Analog process signal | Aux | CTRL Air | DIST | Pres1 | ANALOG1 | -BP01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | PI | [9 empty] | AL |  | ASLL | [9 empty] | =A01QFB01&MFB.001
=A01QJB01WP001 | A01QJB01WP001-BP01 | =A01QJB01WP001-BP01;XQ01 | AUX N2 SUP PIPING PRES1 ANALOG1 | 31 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS NITROGEN SUPPLY SYSTEMS NITROGEN SUPPLY SYSTEM 1 PIPE SYSTEM NITROGEN MAIN DISTRIBUTION 10912; PRESSURE GAUGE WITHOUT PRESSURE REPEATER ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | QJB | Nitrogen Supply Systems | 01 | Nitrogen Supply System 1 | WP | Pipe System | 001 | Nitrogen Main Distribution | -BP01 | 10912; Pressure gauge without pressure repeater | XQ01 | Analog process signal | Aux | N2 Sup | Piping | Pres1 | ANALOG1 | -BP01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | PI | [9 empty] | AL |  | ASLL | [9 empty] | =A01QJB01&MFB.001
=A01QJB01WP003 | A01QJB01WP003-BF10 | =A01QJB01WP003-BF10;XQ01 | AUX N2 SUP PIPING FLOW1 ANALOG1 | 31 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS NITROGEN SUPPLY SYSTEMS NITROGEN SUPPLY SYSTEM 1 PIPE SYSTEM NITROGEN SUPPLY AUX1 10301; FLOWMETER GENERAL ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | QJB | Nitrogen Supply Systems | 01 | Nitrogen Supply System 1 | WP | Pipe System | 003 | Nitrogen Supply AUX1 | -BF10 | 10301; Flowmeter general | XQ01 | Analog process signal | Aux | N2 Sup | Piping | Flow1 | ANALOG1 | -BF10 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | FI | [21 empty] | =A01QJB01&MFB.001
=A01QJB01WP003 | A01QJB01WP003-BF60 | =A01QJB01WP003-BF60;XQ01 | AUX N2 SUP PIPING FLOW6 ANALOG1 | 31 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS NITROGEN SUPPLY SYSTEMS NITROGEN SUPPLY SYSTEM 1 PIPE SYSTEM NITROGEN SUPPLY AUX1 10301; FLOWMETER GENERAL ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | QJB | Nitrogen Supply Systems | 01 | Nitrogen Supply System 1 | WP | Pipe System | 003 | Nitrogen Supply AUX1 | -BF60 | 10301; Flowmeter general | XQ01 | Analog process signal | Aux | N2 Sup | Piping | Flow6 | ANALOG1 | -BF60 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | FI | [21 empty] | =A01QJB01&MFB.001
=A01QJB01WP004 | A01QJB01WP004-BF01 | =A01QJB01WP004-BF01;XQ01 | AUX N2 SUP PIPING FLOW1 ANALOG1 | 31 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS NITROGEN SUPPLY SYSTEMS NITROGEN SUPPLY SYSTEM 1 PIPE SYSTEM NITROGEN SUPPLY AUX2 10301; FLOWMETER GENERAL ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | QJB | Nitrogen Supply Systems | 01 | Nitrogen Supply System 1 | WP | Pipe System | 004 | Nitrogen Supply AUX2 | -BF01 | 10301; Flowmeter general | XQ01 | Analog process signal | Aux | N2 Sup | Piping | Flow1 | ANALOG1 | -BF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | FI | [21 empty] | =A01QJB01&MFB.001
=G01NHA01BZ001 | G01NHA01BZ001-BC01 | =G01NHA01BZ001-BC01;XQ01 | ELY1 RECT1 MEAS1 CURR1 ANALOG1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 1 DC CURRENT MEASUREMENT ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 001 | Measuring System 1 | -BC01 | DC Current Measurement | XQ01 | Analog process signal | Ely1 | Rect1 | Meas1 | Curr1 | ANALOG1 |  | Electrical | 4..20 mA | 4..20 mA | Wire | Undefined |  |  | AI | 0 | IIC | 0 kA | 10 kA
=G01NHA01BZ001 | G01NHA01BZ001-TF01 | =G01NHA01BZ001-TF01;XQ01 | ELY1 RECT1 MEAS1 DC MON1 ANALOG1 | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 1 DC ISOLATION MONITORING ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 001 | Measuring System 1 | -TF01 | DC Isolation Monitoring | XQ01 | Analog process signal | Ely1 | Rect1 | Meas1 | DC MON1 | ANALOG1 |  | Electrical | 4..20 mA | 4..20 mA | Wire | Undefined |  |  | AI | 0 | EIS
=G01NHA01BZ001 | G01NHA01BZ001-TF02 | =G01NHA01BZ001-TF02;XQ01 | ELY1 RECT1 MEAS1 DC MON SIL ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 1 DC CURRENT MEASUREMENT (SIL) ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 001 | Measuring System 1 | -TF02 | DC Current Measurement (SIL) | XQ01 | Analog process signal | Ely1 | Rect1 | Meas1 | DC MON SIL | ANALOG1 | -XG02 | Electrical | 4..20 mA | 4..20 mA | Wire | Undefined |  |  | AI | 1 | IZ | 0 V | 10 V | [15 empty] | B10:XQ01 | EA01 |  | =G01NHA01BZ001-TF02&EFS.008
=G01NHA01BZ002 | G01NHA01BZ002-BC01 | =G01NHA01BZ002-BC01;XQ01 | ELY1 RECT1 MEAS2 CURR1 ANALOG1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 2 DC CURRENT MEASUREMENT ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 002 | Measuring System 2 | -BC01 | DC Current Measurement | XQ01 | Analog process signal | Ely1 | Rect1 | Meas2 | Curr1 | ANALOG1 |  | Electrical | 4..20 mA | 4..20 mA | Wire | Undefined |  |  | AI | 0 | IIC | 0 kA | 10 kA
=G01NHA01BZ002 | G01NHA01BZ002-TF01 | =G01NHA01BZ002-TF01;XQ01 | ELY1 RECT1 MEAS2 DC MON1 ANALOG1 | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 2 DC ISOLATION MONITORING ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 002 | Measuring System 2 | -TF01 | DC Isolation Monitoring | XQ01 | Analog process signal | Ely1 | Rect1 | Meas2 | DC MON1 | ANALOG1 |  | Electrical | 4..20 mA | 4..20 mA | Wire | Undefined |  |  | AI | 0 | EIS
=G01NHA01BZ002 | G01NHA01BZ002-TF02 | =G01NHA01BZ002-TF02;XQ01 | ELY1 RECT1 MEAS2 DC MON SIL ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 2 DC CURRENT MEASUREMENT (SIL) ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 002 | Measuring System 2 | -TF02 | DC Current Measurement (SIL) | XQ01 | Analog process signal | Ely1 | Rect1 | Meas2 | DC MON SIL | ANALOG1 | -XG02 | Electrical | 4..20 mA | 4..20 mA | Wire | Undefined |  |  | AI | 1 | IZ | 0 V | 10 V | [15 empty] | B10:XQ01 | EA01 |  | =G01NHA01BZ002-TF02&EFS.008
=G01NHA01BZ003 | G01NHA01BZ003-BC01 | =G01NHA01BZ003-BC01;XQ01 | ELY1 RECT1 MEAS3 CURR1 ANALOG1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 3 DC CURRENT MEASUREMENT ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 003 | Measuring System 3 | -BC01 | DC Current Measurement | XQ01 | Analog process signal | Ely1 | Rect1 | Meas3 | Curr1 | ANALOG1 |  | Electrical | 4..20 mA | 4..20 mA | Wire | Undefined |  |  | AI | 0 | IIC | 0 kA | 10 kA
=G01NHA01BZ003 | G01NHA01BZ003-TF01 | =G01NHA01BZ003-TF01;XQ01 | ELY1 RECT1 MEAS3 DC MON1 ANALOG1 | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 3 DC ISOLATION MONITORING ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 003 | Measuring System 3 | -TF01 | DC Isolation Monitoring | XQ01 | Analog process signal | Ely1 | Rect1 | Meas3 | DC MON1 | ANALOG1 |  | Electrical | 4..20 mA | 4..20 mA | Wire | Undefined |  |  | AI | 0 | EIS
=G01NHA01BZ003 | G01NHA01BZ003-TF02 | =G01NHA01BZ003-TF02;XQ01 | ELY1 RECT1 MEAS3 DC MON SIL ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 3 DC CURRENT MEASUREMENT (SIL) ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 003 | Measuring System 3 | -TF02 | DC Current Measurement (SIL) | XQ01 | Analog process signal | Ely1 | Rect1 | Meas3 | DC MON SIL | ANALOG1 | -XG02 | Electrical | 4..20 mA | 4..20 mA | Wire | Undefined |  |  | AI | 1 | IZ | 0 V | 10 V | [15 empty] | B10:XQ01 | EA01 |  | =G01NHA01BZ003-TF02&EFS.008
=G01NHA01BZ004 | G01NHA01BZ004-BC01 | =G01NHA01BZ004-BC01;XQ01 | ELY1 RECT1 MEAS4 CURR1 ANALOG1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 4 DC CURRENT MEASUREMENT ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 004 | Measuring System 4 | -BC01 | DC Current Measurement | XQ01 | Analog process signal | Ely1 | Rect1 | Meas4 | Curr1 | ANALOG1 |  | Electrical | 4..20 mA | 4..20 mA | Wire | Undefined |  |  | AI | 0 | IIC | 0 kA | 10 kA
=G01NHA01BZ004 | G01NHA01BZ004-TF01 | =G01NHA01BZ004-TF01;XQ01 | ELY1 RECT1 MEAS4 DC MON1 ANALOG1 | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 4 DC ISOLATION MONITORING ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 004 | Measuring System 4 | -TF01 | DC Isolation Monitoring | XQ01 | Analog process signal | Ely1 | Rect1 | Meas4 | DC MON1 | ANALOG1 |  | Electrical | 4..20 mA | 4..20 mA | Wire | Undefined |  |  | AI | 0 | EIS
=G01NHA01BZ004 | G01NHA01BZ004-TF02 | =G01NHA01BZ004-TF02;XQ01 | ELY1 RECT1 MEAS4 DC MON SIL ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 4 DC CURRENT MEASUREMENT (SIL) ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 004 | Measuring System 4 | -TF02 | DC Current Measurement (SIL) | XQ01 | Analog process signal | Ely1 | Rect1 | Meas4 | DC MON SIL | ANALOG1 | -XG02 | Electrical | 4..20 mA | 4..20 mA | Wire | Undefined |  |  | AI | 1 | IZ | 0 V | 10 V | [15 empty] | B10:XQ01 | EA01 |  | =G01NHA01BZ004-TF02&EFS.008
=G01NHA01EQ001 | G01NHA01EQ001-BP01 | =G01NHA01EQ001-BP01;XQ01 | ELY1 RECT1 COOL PRES1 ANALOG1 | 29 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 COOLING SYSTEMS RECTIFIER COOLING SYSTEM PRESSURE - PUMP INPUT ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | EQ | Cooling Systems | 001 | Rectifier Cooling System | -BP01 | Pressure - Pump Input | XQ01 | Analog process signal | Ely1 | Rect1 | Cool | Pres1 | ANALOG1 | -BP01 | Electrical | 4..20 mA | 4..20 mA | Wire | Undefined |  |  | AI | 0 | PI | [9 empty] | AL |  | ASLL |  |  |  | =G01NHA01KF001+U012UBB01UC001-KF07 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 01 | =G01NHA01EQ001-BP01&EFS.001 | =G01NHA01&MFB.001 |  |  | U012UBB01UC001
=G01NHA01EQ001 | G01NHA01EQ001-BP02 | =G01NHA01EQ001-BP02;XQ01 | ELY1 RECT1 COOL PRES2 ANALOG1 | 29 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 COOLING SYSTEMS RECTIFIER COOLING SYSTEM PRESSURE - PUMP OUTPUT ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | EQ | Cooling Systems | 001 | Rectifier Cooling System | -BP02 | Pressure - Pump Output | XQ01 | Analog process signal | Ely1 | Rect1 | Cool | Pres2 | ANALOG1 | -BP02 | Electrical | 4..20 mA | 4..20 mA | Wire | Undefined |  |  | AI | 0 | PI | [5 empty] | ASHH |  | AH | [7 empty] | =G01NHA01KF001+U012UBB01UC001-KF07 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 02 | =G01NHA01EQ001-BP02&EFS.001 | =G01NHA01&MFB.001 |  |  | U012UBB01UC001
=G01NHA01EQ001 | G01NHA01EQ001-BP03 | =G01NHA01EQ001-BP03;XQ01 | ELY1 RECT1 COOL PRES3 ANALOG1 | 29 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 COOLING SYSTEMS RECTIFIER COOLING SYSTEM PRESSURE - HEAT EXCHANGER OUTPUT ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | EQ | Cooling Systems | 001 | Rectifier Cooling System | -BP03 | Pressure - Heat Exchanger Output | XQ01 | Analog process signal | Ely1 | Rect1 | Cool | Pres3 | ANALOG1 | -BP03 | Electrical | 4..20 mA | 4..20 mA | Wire | Undefined |  |  | AI | 0 | PI | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF07 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 03 | =G01NHA01EQ001-BP03&EFS.001 | =G01NHA01&MFB.001 |  |  | U012UBB01UC001
=G01NHA01EQ001 | G01NHA01EQ001-BQ01 | =G01NHA01EQ001-BQ01;XQ01 | ELY1 RECT1 COOL QUAL1 ANALOG1 | 29 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 COOLING SYSTEMS RECTIFIER COOLING SYSTEM CONDUCTIVITY - HEAT EXCHANGER OUTLET ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | EQ | Cooling Systems | 001 | Rectifier Cooling System | -BQ01 | Conductivity - Heat Exchanger Outlet | XQ01 | Analog process signal | Ely1 | Rect1 | Cool | Qual1 | ANALOG1 | -BQ01 | Electrical | 4..20 mA | 4..20 mA | Wire | Undefined |  |  | AI | 0 | AI | 0 µS/cm | 20 µS/cm | [5 empty] | AH | [7 empty] | =G01NHA01KF001+U012UBB01UC001-KF07 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | XG01:004 | 8 | 04 | =G01NHA01EQ001-BQ01&EFS.001 | =G01NHA01&MFB.001 |  |  | U012UBB01UC001
=G01NHA01EQ001 | G01NHA01EQ001-BQ01 | =G01NHA01EQ001-BQ01;XQ02 | ELY1 RECT1 COOL QUAL1 ANALOG2 | 29 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 COOLING SYSTEMS RECTIFIER COOLING SYSTEM CONDUCTIVITY - HEAT EXCHANGER OUTLET ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | EQ | Cooling Systems | 001 | Rectifier Cooling System | -BQ01 | Conductivity - Heat Exchanger Outlet | XQ02 | Analog process signal | Ely1 | Rect1 | Cool | Qual1 | ANALOG2 | -BQ01 | Electrical | 4..20 mA | 4..20 mA | Wire | Undefined |  |  | AI | 0 | TI | 0 µS/cm | 20 µS/cm | [13 empty] | =G01NHA01KF001+U012UBB01UC001-KF07 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ02 | EA01 | 05 | =G01NHA01EQ001-BQ01&EFS.001 | =G01NHA01&MFB.001 |  |  | U012UBB01UC001
=G01NHA01EQ001 | G01NHA01EQ001-BT01 | =G01NHA01EQ001-BT01;XQ01 | ELY1 RECT1 COOL TEMP1 ANALOG1 | 29 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 COOLING SYSTEMS RECTIFIER COOLING SYSTEM TEMPERATURE - HEAT EXCHANGER OUTLET ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | EQ | Cooling Systems | 001 | Rectifier Cooling System | -BT01 | Temperature - Heat Exchanger Outlet | XQ01 | Analog process signal | Ely1 | Rect1 | Cool | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Undefined |  |  | AI | 0 | TI | -20 °C | 80 °C |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHA01KF001+U012UBB01UC001-KF07 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 06 | =G01NHA01EQ001-BT01&EFS.001 | =G01NHA01&MFB.001 |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-BT01 | =G01NHA01TA001-BT01;XQ01 | ELY1 RECT1 TRAFO1 TEMP1 ANALOG1 | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER TEMPERATURE SWITCH - OIL TEMPERATURE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BT01 | Temperature switch - Oil temperature | XQ01 | Analog process signal | Ely1 | Rect1 | Trafo1 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Undefined |  |  | AI | 0 | TI | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF07 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 07 | =G01NHA01TA001-BT01&EFS.011 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-BT02 | =G01NHA01TA001-BT02;XQ01 | ELY1 RECT1 TRAFO1 TEMP2 ANALOG1 | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER TEMPERATURE SWITCH - WINDING TEMPERATURE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BT02 | Temperature switch - Winding temperature | XQ01 | Analog process signal | Ely1 | Rect1 | Trafo1 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Undefined |  |  | AI | 0 | TIZ | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF07 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 08 | =G01NHA01TA001-BT02&EFS.011 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-BT10 | =G01NHA01TA001-BT10;XQ01 | ELY1 RECT1 TRAFO1 OIL TEMP1 ANALOG1 | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER PT100 - TOP OIL TEMPERATURE TEMPERATURE - TOP OIL TRANSFORMER | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BT10 | PT100 - Top Oil Temperature | XQ01 | Temperature - Top Oil Transformer | Ely1 | Rect1 | Trafo1 | Oil Temp1 | ANALOG1 | DR | Electrical | PT100 | PT100 | Wire | Undefined |  |  | AI | 0 | TI | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF08 | 6DL1 134-6JH00-0EH1, ET 200SP HA, AI 16XTC/8XRTD 2-/3-/4-WIRE | B10:XQ01 | EA01 | 02 | =G01NHA01TA001-BT10&EFS.012 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-BT11 | =G01NHA01TA001-BT11;XQ01 | ELY1 RECT1 TRAFO1 OIL TEMP2 ANALOG1 | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER PT100 - TOP OIL TEMPERATURE TEMPERATURE - TOP OIL TRANSFORMER | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BT11 | PT100 - Top Oil Temperature | XQ01 | Temperature - Top Oil Transformer | Ely1 | Rect1 | Trafo1 | Oil Temp2 | ANALOG1 | DR | Electrical | PT100 | PT100 | Wire | Undefined |  |  | AI | 0 | TI | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF08 | 6DL1 134-6JH00-0EH1, ET 200SP HA, AI 16XTC/8XRTD 2-/3-/4-WIRE | B10:XQ01 | EA01 | 03 | =G01NHA01TA001-BT11&EFS.012 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-BT20 | =G01NHA01TA001-BT20;XQ01 | ELY1 RECT1 TRAFO1 COOL TEMP1 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER PT100 - COOLING WATER INLET TEMPERATURE - COOLING WATER INLET | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BT20 | PT100 - Cooling Water Inlet | XQ01 | Temperature - Cooling water inlet | Ely1 | Rect1 | Trafo1 | Cool Temp1 | ANALOG1 | DR | Electrical | PT100 | PT100 | Wire | Undefined |  |  | AI | 0 | TI | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF08 | 6DL1 134-6JH00-0EH1, ET 200SP HA, AI 16XTC/8XRTD 2-/3-/4-WIRE | B10:XQ01 | EA01 | 04 | =G01NHA01TA001-BT20&EFS.017 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-BT21 | =G01NHA01TA001-BT21;XQ01 | ELY1 RECT1 TRAFO1 COOL TEMP2 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER PT100 - COOLING WATER OUTLET TEMPERATURE - COOLING WATER OUTLET | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BT21 | PT100 - Cooling Water Outlet | XQ01 | Temperature - Cooling water outlet | Ely1 | Rect1 | Trafo1 | Cool Temp2 | ANALOG1 | DR | Electrical | PT100 | PT100 | Wire | Undefined |  |  | AI | 0 | TI | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF08 | 6DL1 134-6JH00-0EH1, ET 200SP HA, AI 16XTC/8XRTD 2-/3-/4-WIRE | B10:XQ01 | EA01 | 05 | =G01NHA01TA001-BT21&EFS.018 |  |  |  | U012UBB01UC001
=G01NHA01WP001 | G01NHA01WP001-BT03 | =G01NHA01WP001-BT03;XQ01 | ELY1 RECT1 PIPING TEMP3 ANALOG1 | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 PIPE SYSTEM PIPE SYSTEM 1 TEMPERATURE MEASUREMENT - COOLING WATER ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | WP | Pipe System | 001 | Pipe System 1 | -BT03 | Temperature Measurement - Cooling Water | XQ01 | Analog process signal | Ely1 | Rect1 | Piping | Temp3 | ANALOG1 | -BT03 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | -20 °C | 100 °C | [13 empty] | =G01NHY01KF001+U012UNA01UH100-KF13 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 10 |  | =G01NHA01&MFB.001 |  |  | U012UNA01UH100
=G01NHA01WP001 | G01NHA01WP001-BT04 | =G01NHA01WP001-BT04;XQ01 | ELY1 RECT1 PIPING TEMP4 ANALOG1 | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 PIPE SYSTEM PIPE SYSTEM 1 TEMPERATURE MEASUREMENT - COOLING WATER ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | WP | Pipe System | 001 | Pipe System 1 | -BT04 | Temperature Measurement - Cooling Water | XQ01 | Analog process signal | Ely1 | Rect1 | Piping | Temp4 | ANALOG1 | -BT04 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | -20 °C | 100 °C | [13 empty] | =G01NHY01KF001+U012UNA01UH100-KF13 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 11 |  | =G01NHA01&MFB.001 |  |  | U012UNA01UH100
=G01NHB01EQ001 | G01NHB01EQ001-BQ01 | =G01NHB01EQ001-BQ01;XQ01 | ELY1 GRP1 COOL QUAL1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ01 | Conductivity WP H2 | XQ01 | Analog process signal | Ely1 | Grp1 | Cool | Qual1 | ANALOG1 | -BQ01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | AI | 0 µS/cm | 20 µS/cm |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB01KF002+U012UNA01UH111-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | XQ01B | 01 | =G01NHB01EQ001-BQ01&EFS.001 | =G01NHB01&MFB.001 |  |  | U012UNA01UH111
=G01NHB01EQ001 | G01NHB01EQ001-BQ01 | =G01NHB01EQ001-BQ01;XQ02 | ELY1 GRP1 COOL QUAL1 ANALOG2 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ01 | Conductivity WP H2 | XQ02 | Analog process signal | Ely1 | Grp1 | Cool | Qual1 | ANALOG2 | -BQ01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | 0 µS/cm | 20 µS/cm | [7 empty] | AL |  | ASLL |  |  |  | =G01NHB01KF002+U012UNA01UH111-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ02 | XQ02B | 02 | =G01NHB01EQ001-BQ01&EFS.001 | =G01NHB01&MFB.001 |  |  | U012UNA01UH111
=G01NHB01EQ001 | G01NHB01EQ001-BQ02 | =G01NHB01EQ001-BQ02;XQ01 | ELY1 GRP1 COOL QUAL2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ02 | Conductivity WP O2 | XQ01 | Analog process signal | Ely1 | Grp1 | Cool | Qual2 | ANALOG1 | -BQ02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | AI | 0 µS/cm | 20 µS/cm |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB01KF002+U012UNA01UH111-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | XQ01B | 03 | =G01NHB01EQ001-BQ02&EFS.001 | =G01NHB01&MFB.001 |  |  | U012UNA01UH111
=G01NHB01EQ001 | G01NHB01EQ001-BQ02 | =G01NHB01EQ001-BQ02;XQ02 | ELY1 GRP1 COOL QUAL2 ANALOG2 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ02 | Conductivity WP O2 | XQ02 | Analog process signal | Ely1 | Grp1 | Cool | Qual2 | ANALOG2 | -BQ02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | 0 µS/cm | 20 µS/cm | [7 empty] | AL |  | ASLL |  |  |  | =G01NHB01KF002+U012UNA01UH111-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ02 | XQ02B | 04 | =G01NHB01EQ001-BQ02&EFS.001 | =G01NHB01&MFB.001 |  |  | U012UNA01UH111
=G01NHB01EQ001 | G01NHB01EQ001-BT01 | =G01NHB01EQ001-BT01;XQ01 | ELY1 GRP1 COOL TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 TEMPERATURE WCR ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BT01 | Temperature WCR | XQ01 | Analog process signal | Ely1 | Grp1 | Cool | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | -20 °C | 100 °C | [13 empty] | =G01NHB01KF002+U012UNA01UH111-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 05 | =G01NHB01EQ001-BT01&EFS.001 | =G01NHB01&MFB.001 |  |  | U012UNA01UH111
=G01NHB01EQ001 | G01NHB01EQ001-BT02 | =G01NHB01EQ001-BT02;XQ01 | ELY1 GRP1 COOL TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 TEMPERATURE WP H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BT02 | Temperature WP H2 | XQ01 | Analog process signal | Ely1 | Grp1 | Cool | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | TI | -20 °C | 100 °C | [5 empty] | AZH |  | AZL |  |  |  | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF04 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | XG02:1 | 1A | 01 | =G01NHB01EQ001-BT02&EFS.001 | =G01NHB01&MFB.001 |  |  | U012UNA01UH100
=G01NHB01EQ001 | G01NHB01EQ001-BT03 | =G01NHB01EQ001-BT03;XQ01 | ELY1 GRP1 COOL TEMP3 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 TEMPERATURE WP O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BT03 | Temperature WP O2 | XQ01 | Analog process signal | Ely1 | Grp1 | Cool | Temp3 | ANALOG1 | -BT03 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | TI | -20 °C | 100 °C | [5 empty] | AZH |  | AZL |  |  |  | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF04 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | XG02:3 | 3A | 02 | =G01NHB01EQ001-BT03&EFS.001 | =G01NHB01&MFB.001 |  |  | U012UNA01UH100
=G01NHB01EQ001 | G01NHB01EQ001-QN01 | =G01NHB01EQ001-QN01;XQ01 | ELY1 GRP1 COOL CV1 ANALOG1 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 COOLING WATER - CONTROL VALVE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -QN01 | Cooling Water - Control Valve | XQ01 | Analog process signal | Ely1 | Grp1 | Cool | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | G | [15 empty] | =G01NHB01KF002+U012UNA01UH111-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART |  |  | 14 | =G01NHB01EQ001-QN01&EFS.001 | =G01NHB01&MFB.001 |  |  | U012UNA01UH111
=G01NHB01HT001 | G01NHB01HT001-BT01 | =G01NHB01HT001-BT01;XQ01 | ELY1 GRP1 MOD1 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 ELECTROLYSIS MODULES MODULE 1 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | HT | Electrolysis Modules | 001 | Module 1 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp1 | Mod1 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB01KF002+U012UNA01UH111-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 06 | =G01NHB01HT001-BT01&EFS.001 | =G01NHB01&MFB.001 |  |  | U012UNA01UH111
=G01NHB01HT001 | G01NHB01HT001-BT02 | =G01NHB01HT001-BT02;XQ01 | ELY1 GRP1 MOD1 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 ELECTROLYSIS MODULES MODULE 1 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | HT | Electrolysis Modules | 001 | Module 1 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp1 | Mod1 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB01KF002+U012UNA01UH111-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | 1 | 07 | =G01NHB01HT001-BT02&EFS.001 | =G01NHB01&MFB.001 |  |  | U012UNA01UH111
=G01NHB01HT002 | G01NHB01HT002-BT01 | =G01NHB01HT002-BT01;XQ01 | ELY1 GRP1 MOD2 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 ELECTROLYSIS MODULES MODULE 2 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | HT | Electrolysis Modules | 002 | Module 2 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp1 | Mod2 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB01KF002+U012UNA01UH111-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 08 | =G01NHB01HT002-BT01&EFS.001 | =G01NHB01&MFB.001 |  |  | U012UNA01UH111
=G01NHB01HT002 | G01NHB01HT002-BT02 | =G01NHB01HT002-BT02;XQ01 | ELY1 GRP1 MOD2 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 ELECTROLYSIS MODULES MODULE 2 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | HT | Electrolysis Modules | 002 | Module 2 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp1 | Mod2 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB01KF002+U012UNA01UH111-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 09 | =G01NHB01HT002-BT02&EFS.001 | =G01NHB01&MFB.001 |  |  | U012UNA01UH111
=G01NHB01HT003 | G01NHB01HT003-BT01 | =G01NHB01HT003-BT01;XQ01 | ELY1 GRP1 MOD3 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 ELECTROLYSIS MODULES MODULE 3 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | HT | Electrolysis Modules | 003 | Module 3 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp1 | Mod3 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB01KF002+U012UNA01UH111-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 10 | =G01NHB01HT003-BT01&EFS.001 | =G01NHB01&MFB.001 |  |  | U012UNA01UH111
=G01NHB01HT003 | G01NHB01HT003-BT02 | =G01NHB01HT003-BT02;XQ01 | ELY1 GRP1 MOD3 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 ELECTROLYSIS MODULES MODULE 3 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | HT | Electrolysis Modules | 003 | Module 3 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp1 | Mod3 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB01KF002+U012UNA01UH111-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 11 | =G01NHB01HT003-BT02&EFS.001 | =G01NHB01&MFB.001 |  |  | U012UNA01UH111
=G01NHB01HT004 | G01NHB01HT004-BT01 | =G01NHB01HT004-BT01;XQ01 | ELY1 GRP1 MOD4 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 ELECTROLYSIS MODULES MODULE 4 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | HT | Electrolysis Modules | 004 | Module 4 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp1 | Mod4 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB01KF002+U012UNA01UH111-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 12 | =G01NHB01HT004-BT01&EFS.001 | =G01NHB01&MFB.001 |  |  | U012UNA01UH111
=G01NHB01HT004 | G01NHB01HT004-BT02 | =G01NHB01HT004-BT02;XQ01 | ELY1 GRP1 MOD4 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 ELECTROLYSIS MODULES MODULE 4 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | HT | Electrolysis Modules | 004 | Module 4 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp1 | Mod4 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB01KF002+U012UNA01UH111-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART |  |  | 13 | =G01NHB01HT004-BT02&EFS.001 | =G01NHB01&MFB.001 |  |  | U012UNA01UH111
=G01NHB01KF001 | G01NHB01KF001-BA01 | =G01NHB01KF001-BA01;XQ01 | ELY1 GRP1 CTRL U1 CELL VOLT1 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 CELL -VOLTAGE MODULE 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | XQ01 | Cell -Voltage Module 1 | Ely1 | Grp1 | CTRL U1 | Cell Volt1 | ANALOG1 | BA01 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB01KF001+U012UNA01UH112-KF02 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 01 | =G01NHB01KF001&EFS.053 | =G01NHB01&MFB.001 |  |  | U012UNA01UH112
=G01NHB01KF001 | G01NHB01KF001-BA02 | =G01NHB01KF001-BA02;XQ01 | ELY1 GRP1 CTRL U1 CELL VOLT2 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 2 CELL -VOLTAGE MODULE 2 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | KF | Control Units | 001 | Cell Voltage Measurement | -BA02 | Cell-Voltage-Measurement - Module 2 | XQ01 | Cell -Voltage Module 2 | Ely1 | Grp1 | CTRL U1 | Cell Volt2 | ANALOG1 | BA02 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB01KF001+U012UNA01UH112-KF02 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 02 | =G01NHB01KF001&EFS.053 | =G01NHB01&MFB.001 |  |  | U012UNA01UH112
=G01NHB01KF001 | G01NHB01KF001-BA03 | =G01NHB01KF001-BA03;XQ01 | ELY1 GRP1 CTRL U1 CELL VOLT3 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 3 CELL -VOLTAGE MODULE 3 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | KF | Control Units | 001 | Cell Voltage Measurement | -BA03 | Cell-Voltage-Measurement - Module 3 | XQ01 | Cell -Voltage Module 3 | Ely1 | Grp1 | CTRL U1 | Cell Volt3 | ANALOG1 | BA03 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB01KF001+U012UNA01UH112-KF03 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 01 | =G01NHB01KF001&EFS.053 | =G01NHB01&MFB.001 |  |  | U012UNA01UH112
=G01NHB01KF001 | G01NHB01KF001-BA04 | =G01NHB01KF001-BA04;XQ01 | ELY1 GRP1 CTRL U1 CELL VOLT4 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 4 CELL -VOLTAGE MODULE 4 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | KF | Control Units | 001 | Cell Voltage Measurement | -BA04 | Cell-Voltage-Measurement - Module 4 | XQ01 | Cell -Voltage Module 4 | Ely1 | Grp1 | CTRL U1 | Cell Volt4 | ANALOG1 | BA04 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB01KF001+U012UNA01UH112-KF03 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 02 | =G01NHB01KF001&EFS.053 | =G01NHB01&MFB.001 |  |  | U012UNA01UH112
=G01NHB02EQ001 | G01NHB02EQ001-BQ01 | =G01NHB02EQ001-BQ01;XQ01 | ELY1 GRP2 COOL QUAL1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ01 | Conductivity WP H2 | XQ01 | Analog process signal | Ely1 | Grp2 | Cool | Qual1 | ANALOG1 | -BQ01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | AI | 0 µS/cm | 20 µS/cm |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB02KF002+U012UNA01UH121-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | XQ01B | 01 | =G01NHB02EQ001-BQ01&EFS.001 | =G01NHB02&MFB.001 |  |  | U012UNA01UH121
=G01NHB02EQ001 | G01NHB02EQ001-BQ01 | =G01NHB02EQ001-BQ01;XQ02 | ELY1 GRP2 COOL QUAL1 ANALOG2 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ01 | Conductivity WP H2 | XQ02 | Analog process signal | Ely1 | Grp2 | Cool | Qual1 | ANALOG2 | -BQ01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | 0 µS/cm | 20 µS/cm | [7 empty] | AL |  | ASLL |  |  |  | =G01NHB02KF002+U012UNA01UH121-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ02 | XQ02B | 02 | =G01NHB02EQ001-BQ01&EFS.001 | =G01NHB02&MFB.001 |  |  | U012UNA01UH121
=G01NHB02EQ001 | G01NHB02EQ001-BQ02 | =G01NHB02EQ001-BQ02;XQ01 | ELY1 GRP2 COOL QUAL2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ02 | Conductivity WP O2 | XQ01 | Analog process signal | Ely1 | Grp2 | Cool | Qual2 | ANALOG1 | -BQ02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | AI | 0 µS/cm | 20 µS/cm |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB02KF002+U012UNA01UH121-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | XQ01B | 03 | =G01NHB02EQ001-BQ02&EFS.001 | =G01NHB02&MFB.001 |  |  | U012UNA01UH121
=G01NHB02EQ001 | G01NHB02EQ001-BQ02 | =G01NHB02EQ001-BQ02;XQ02 | ELY1 GRP2 COOL QUAL2 ANALOG2 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ02 | Conductivity WP O2 | XQ02 | Analog process signal | Ely1 | Grp2 | Cool | Qual2 | ANALOG2 | -BQ02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | 0 µS/cm | 20 µS/cm | [7 empty] | AL |  | ASLL |  |  |  | =G01NHB02KF002+U012UNA01UH121-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ02 | XQ02B | 04 | =G01NHB02EQ001-BQ02&EFS.001 | =G01NHB02&MFB.001 |  |  | U012UNA01UH121
=G01NHB02EQ001 | G01NHB02EQ001-BT01 | =G01NHB02EQ001-BT01;XQ01 | ELY1 GRP2 COOL TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 TEMPERATURE WCR ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BT01 | Temperature WCR | XQ01 | Analog process signal | Ely1 | Grp2 | Cool | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | -20 °C | 100 °C | [13 empty] | =G01NHB02KF002+U012UNA01UH121-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 05 | =G01NHB02EQ001-BT01&EFS.001 | =G01NHB02&MFB.001 |  |  | U012UNA01UH121
=G01NHB02EQ001 | G01NHB02EQ001-BT02 | =G01NHB02EQ001-BT02;XQ01 | ELY1 GRP2 COOL TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 TEMPERATURE WP H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BT02 | Temperature WP H2 | XQ01 | Analog process signal | Ely1 | Grp2 | Cool | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | TI | -20 °C | 100 °C | [5 empty] | AZH |  | AZL |  |  |  | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF04 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | XG02:1 | 1A | 03 | =G01NHB02EQ001-BT02&EFS.001 | =G01NHB02&MFB.001 |  |  | U012UNA01UH100
=G01NHB02EQ001 | G01NHB02EQ001-BT03 | =G01NHB02EQ001-BT03;XQ01 | ELY1 GRP2 COOL TEMP3 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 TEMPERATURE WP O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BT03 | Temperature WP O2 | XQ01 | Analog process signal | Ely1 | Grp2 | Cool | Temp3 | ANALOG1 | -BT03 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | TI | -20 °C | 100 °C | [5 empty] | AZH |  | AZL |  |  |  | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF04 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | XG02:3 | 3A | 04 | =G01NHB02EQ001-BT03&EFS.001 | =G01NHB02&MFB.001 |  |  | U012UNA01UH100
=G01NHB02EQ001 | G01NHB02EQ001-QN01 | =G01NHB02EQ001-QN01;XQ01 | ELY1 GRP2 COOL CV1 ANALOG1 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 COOLING WATER - CONTROL VALVE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -QN01 | Cooling Water - Control Valve | XQ01 | Analog process signal | Ely1 | Grp2 | Cool | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | G | [15 empty] | =G01NHB02KF002+U012UNA01UH121-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 14 | =G01NHB02EQ001-QN01&EFS.001 | =G01NHB02&MFB.001 |  |  | U012UNA01UH121
=G01NHB02HT001 | G01NHB02HT001-BT01 | =G01NHB02HT001-BT01;XQ01 | ELY1 GRP2 MOD1 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 ELECTROLYSIS MODULES MODULE 1 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | HT | Electrolysis Modules | 001 | Module 1 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp2 | Mod1 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB02KF002+U012UNA01UH121-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 06 | =G01NHB02HT001-BT01&EFS.001 | =G01NHB02&MFB.001 |  |  | U012UNA01UH121
=G01NHB02HT001 | G01NHB02HT001-BT02 | =G01NHB02HT001-BT02;XQ01 | ELY1 GRP2 MOD1 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 ELECTROLYSIS MODULES MODULE 1 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | HT | Electrolysis Modules | 001 | Module 1 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp2 | Mod1 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB02KF002+U012UNA01UH121-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 07 | =G01NHB02HT001-BT02&EFS.001 | =G01NHB02&MFB.001 |  |  | U012UNA01UH121
=G01NHB02HT002 | G01NHB02HT002-BT01 | =G01NHB02HT002-BT01;XQ01 | ELY1 GRP2 MOD2 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 ELECTROLYSIS MODULES MODULE 2 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | HT | Electrolysis Modules | 002 | Module 2 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp2 | Mod2 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB02KF002+U012UNA01UH121-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 08 | =G01NHB02HT002-BT01&EFS.001 | =G01NHB02&MFB.001 |  |  | U012UNA01UH121
=G01NHB02HT002 | G01NHB02HT002-BT02 | =G01NHB02HT002-BT02;XQ01 | ELY1 GRP2 MOD2 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 ELECTROLYSIS MODULES MODULE 2 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | HT | Electrolysis Modules | 002 | Module 2 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp2 | Mod2 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB02KF002+U012UNA01UH121-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 09 | =G01NHB02HT002-BT02&EFS.001 | =G01NHB02&MFB.001 |  |  | U012UNA01UH121
=G01NHB02HT003 | G01NHB02HT003-BT01 | =G01NHB02HT003-BT01;XQ01 | ELY1 GRP2 MOD3 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 ELECTROLYSIS MODULES MODULE 3 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | HT | Electrolysis Modules | 003 | Module 3 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp2 | Mod3 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB02KF002+U012UNA01UH121-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 10 | =G01NHB02HT003-BT01&EFS.001 | =G01NHB02&MFB.001 |  |  | U012UNA01UH121
=G01NHB02HT003 | G01NHB02HT003-BT02 | =G01NHB02HT003-BT02;XQ01 | ELY1 GRP2 MOD3 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 ELECTROLYSIS MODULES MODULE 3 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | HT | Electrolysis Modules | 003 | Module 3 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp2 | Mod3 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB02KF002+U012UNA01UH121-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 11 | =G01NHB02HT003-BT02&EFS.001 | =G01NHB02&MFB.001 |  |  | U012UNA01UH121
=G01NHB02HT004 | G01NHB02HT004-BT01 | =G01NHB02HT004-BT01;XQ01 | ELY1 GRP2 MOD4 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 ELECTROLYSIS MODULES MODULE 4 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | HT | Electrolysis Modules | 004 | Module 4 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp2 | Mod4 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB02KF002+U012UNA01UH121-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 12 | =G01NHB02HT004-BT01&EFS.001 | =G01NHB02&MFB.001 |  |  | U012UNA01UH121
=G01NHB02HT004 | G01NHB02HT004-BT02 | =G01NHB02HT004-BT02;XQ01 | ELY1 GRP2 MOD4 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 ELECTROLYSIS MODULES MODULE 4 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | HT | Electrolysis Modules | 004 | Module 4 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp2 | Mod4 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB02KF002+U012UNA01UH121-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 13 | =G01NHB02HT004-BT02&EFS.001 | =G01NHB02&MFB.001 |  |  | U012UNA01UH121
=G01NHB02KF001 | G01NHB02KF001-BA01 | =G01NHB02KF001-BA01;XQ01 | ELY1 GRP2 CTRL U1 CELL VOLT1 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 CELL -VOLTAGE MODULE 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | XQ01 | Cell -Voltage Module 1 | Ely1 | Grp2 | CTRL U1 | Cell Volt1 | ANALOG1 | BA01 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB02KF001+U012UNA01UH122-KF02 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 01 | =G01NHB02KF001&EFS.053 | =G01NHB02&MFB.001 |  |  | U012UNA01UH122
=G01NHB02KF001 | G01NHB02KF001-BA02 | =G01NHB02KF001-BA02;XQ01 | ELY1 GRP2 CTRL U1 CELL VOLT2 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 2 CELL -VOLTAGE MODULE 2 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | KF | Control Units | 001 | Cell Voltage Measurement | -BA02 | Cell-Voltage-Measurement - Module 2 | XQ01 | Cell -Voltage Module 2 | Ely1 | Grp2 | CTRL U1 | Cell Volt2 | ANALOG1 | BA02 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB02KF001+U012UNA01UH122-KF02 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 02 | =G01NHB02KF001&EFS.053 | =G01NHB02&MFB.001 |  |  | U012UNA01UH122
=G01NHB02KF001 | G01NHB02KF001-BA03 | =G01NHB02KF001-BA03;XQ01 | ELY1 GRP2 CTRL U1 CELL VOLT3 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 3 CELL -VOLTAGE MODULE 3 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | KF | Control Units | 001 | Cell Voltage Measurement | -BA03 | Cell-Voltage-Measurement - Module 3 | XQ01 | Cell -Voltage Module 3 | Ely1 | Grp2 | CTRL U1 | Cell Volt3 | ANALOG1 | BA03 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB02KF001+U012UNA01UH122-KF03 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 01 | =G01NHB02KF001&EFS.053 | =G01NHB02&MFB.001 |  |  | U012UNA01UH122
=G01NHB02KF001 | G01NHB02KF001-BA04 | =G01NHB02KF001-BA04;XQ01 | ELY1 GRP2 CTRL U1 CELL VOLT4 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 4 CELL -VOLTAGE MODULE 4 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | KF | Control Units | 001 | Cell Voltage Measurement | -BA04 | Cell-Voltage-Measurement - Module 4 | XQ01 | Cell -Voltage Module 4 | Ely1 | Grp2 | CTRL U1 | Cell Volt4 | ANALOG1 | BA04 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB02KF001+U012UNA01UH122-KF03 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 02 | =G01NHB02KF001&EFS.053 | =G01NHB02&MFB.001 |  |  | U012UNA01UH122
=G01NHB03EQ001 | G01NHB03EQ001-BQ01 | =G01NHB03EQ001-BQ01;XQ01 | ELY1 GRP3 COOL QUAL1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ01 | Conductivity WP H2 | XQ01 | Analog process signal | Ely1 | Grp3 | Cool | Qual1 | ANALOG1 | -BQ01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | AI | 0 µS/cm | 20 µS/cm |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB03KF002+U012UNA01UH131-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | XQ01B | 01 | =G01NHB03EQ001-BQ01&EFS.001 | =G01NHB03&MFB.001 |  |  | U012UNA01UH131
=G01NHB03EQ001 | G01NHB03EQ001-BQ01 | =G01NHB03EQ001-BQ01;XQ02 | ELY1 GRP3 COOL QUAL1 ANALOG2 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ01 | Conductivity WP H2 | XQ02 | Analog process signal | Ely1 | Grp3 | Cool | Qual1 | ANALOG2 | -BQ01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | 0 µS/cm | 20 µS/cm | [7 empty] | AL |  | ASLL |  |  |  | =G01NHB03KF002+U012UNA01UH131-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ02 | XQ02B | 02 | =G01NHB03EQ001-BQ01&EFS.001 | =G01NHB03&MFB.001 |  |  | U012UNA01UH131
=G01NHB03EQ001 | G01NHB03EQ001-BQ02 | =G01NHB03EQ001-BQ02;XQ01 | ELY1 GRP3 COOL QUAL2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ02 | Conductivity WP O2 | XQ01 | Analog process signal | Ely1 | Grp3 | Cool | Qual2 | ANALOG1 | -BQ02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | AI | 0 µS/cm | 20 µS/cm |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB03KF002+U012UNA01UH131-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | XQ01B | 03 | =G01NHB03EQ001-BQ02&EFS.001 | =G01NHB03&MFB.001 |  |  | U012UNA01UH131
=G01NHB03EQ001 | G01NHB03EQ001-BQ02 | =G01NHB03EQ001-BQ02;XQ02 | ELY1 GRP3 COOL QUAL2 ANALOG2 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ02 | Conductivity WP O2 | XQ02 | Analog process signal | Ely1 | Grp3 | Cool | Qual2 | ANALOG2 | -BQ02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | 0 µS/cm | 20 µS/cm | [7 empty] | AL |  | ASLL |  |  |  | =G01NHB03KF002+U012UNA01UH131-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ02 | XQ02B | 04 | =G01NHB03EQ001-BQ02&EFS.001 | =G01NHB03&MFB.001 |  |  | U012UNA01UH131
=G01NHB03EQ001 | G01NHB03EQ001-BT01 | =G01NHB03EQ001-BT01;XQ01 | ELY1 GRP3 COOL TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 TEMPERATURE WCR ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BT01 | Temperature WCR | XQ01 | Analog process signal | Ely1 | Grp3 | Cool | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | -20 °C | 100 °C | [13 empty] | =G01NHB03KF002+U012UNA01UH131-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 05 | =G01NHB03EQ001-BT01&EFS.001 | =G01NHB03&MFB.001 |  |  | U012UNA01UH131
=G01NHB03EQ001 | G01NHB03EQ001-BT02 | =G01NHB03EQ001-BT02;XQ01 | ELY1 GRP3 COOL TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 TEMPERATURE WP H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BT02 | Temperature WP H2 | XQ01 | Analog process signal | Ely1 | Grp3 | Cool | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | TI | -20 °C | 100 °C | [5 empty] | AZH |  | AZL |  |  |  | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF04 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | XG02:1 | 1A | 05 | =G01NHB03EQ001-BT02&EFS.001 | =G01NHB03&MFB.001 |  |  | U012UNA01UH100
=G01NHB03EQ001 | G01NHB03EQ001-BT03 | =G01NHB03EQ001-BT03;XQ01 | ELY1 GRP3 COOL TEMP3 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 TEMPERATURE WP O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BT03 | Temperature WP O2 | XQ01 | Analog process signal | Ely1 | Grp3 | Cool | Temp3 | ANALOG1 | -BT03 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | TI | -20 °C | 100 °C | [5 empty] | AZH |  | AZL |  |  |  | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF04 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | XG02:3 | 3A | 06 | =G01NHB03EQ001-BT03&EFS.001 | =G01NHB03&MFB.001 |  |  | U012UNA01UH100
=G01NHB03EQ001 | G01NHB03EQ001-QN01 | =G01NHB03EQ001-QN01;XQ01 | ELY1 GRP3 COOL CV1 ANALOG1 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 COOLING WATER - CONTROL VALVE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -QN01 | Cooling Water - Control Valve | XQ01 | Analog process signal | Ely1 | Grp3 | Cool | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | G | [15 empty] | =G01NHB03KF002+U012UNA01UH131-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 14 | =G01NHB03EQ001-QN01&EFS.001 | =G01NHB03&MFB.001 |  |  | U012UNA01UH131
=G01NHB03HT001 | G01NHB03HT001-BT01 | =G01NHB03HT001-BT01;XQ01 | ELY1 GRP3 MOD1 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 ELECTROLYSIS MODULES MODULE 1 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | HT | Electrolysis Modules | 001 | Module 1 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp3 | Mod1 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB03KF002+U012UNA01UH131-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 06 | =G01NHB03HT001-BT01&EFS.001 | =G01NHB03&MFB.001 |  |  | U012UNA01UH131
=G01NHB03HT001 | G01NHB03HT001-BT02 | =G01NHB03HT001-BT02;XQ01 | ELY1 GRP3 MOD1 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 ELECTROLYSIS MODULES MODULE 1 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | HT | Electrolysis Modules | 001 | Module 1 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp3 | Mod1 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB03KF002+U012UNA01UH131-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 07 | =G01NHB03HT001-BT02&EFS.001 | =G01NHB03&MFB.001 |  |  | U012UNA01UH131
=G01NHB03HT002 | G01NHB03HT002-BT01 | =G01NHB03HT002-BT01;XQ01 | ELY1 GRP3 MOD2 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 ELECTROLYSIS MODULES MODULE 2 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | HT | Electrolysis Modules | 002 | Module 2 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp3 | Mod2 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB03KF002+U012UNA01UH131-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 08 | =G01NHB03HT002-BT01&EFS.001 | =G01NHB03&MFB.001 |  |  | U012UNA01UH131
=G01NHB03HT002 | G01NHB03HT002-BT02 | =G01NHB03HT002-BT02;XQ01 | ELY1 GRP3 MOD2 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 ELECTROLYSIS MODULES MODULE 2 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | HT | Electrolysis Modules | 002 | Module 2 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp3 | Mod2 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB03KF002+U012UNA01UH131-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 09 | =G01NHB03HT002-BT02&EFS.001 | =G01NHB03&MFB.001 |  |  | U012UNA01UH131
=G01NHB03HT003 | G01NHB03HT003-BT01 | =G01NHB03HT003-BT01;XQ01 | ELY1 GRP3 MOD3 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 ELECTROLYSIS MODULES MODULE 3 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | HT | Electrolysis Modules | 003 | Module 3 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp3 | Mod3 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB03KF002+U012UNA01UH131-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 10 | =G01NHB03HT003-BT01&EFS.001 | =G01NHB03&MFB.001 |  |  | U012UNA01UH131
=G01NHB03HT003 | G01NHB03HT003-BT02 | =G01NHB03HT003-BT02;XQ01 | ELY1 GRP3 MOD3 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 ELECTROLYSIS MODULES MODULE 3 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | HT | Electrolysis Modules | 003 | Module 3 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp3 | Mod3 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB03KF002+U012UNA01UH131-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 11 | =G01NHB03HT003-BT02&EFS.001 | =G01NHB03&MFB.001 |  |  | U012UNA01UH131
=G01NHB03HT004 | G01NHB03HT004-BT01 | =G01NHB03HT004-BT01;XQ01 | ELY1 GRP3 MOD4 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 ELECTROLYSIS MODULES MODULE 4 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | HT | Electrolysis Modules | 004 | Module 4 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp3 | Mod4 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB03KF002+U012UNA01UH131-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 12 | =G01NHB03HT004-BT01&EFS.001 | =G01NHB03&MFB.001 |  |  | U012UNA01UH131
=G01NHB03HT004 | G01NHB03HT004-BT02 | =G01NHB03HT004-BT02;XQ01 | ELY1 GRP3 MOD4 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 ELECTROLYSIS MODULES MODULE 4 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | HT | Electrolysis Modules | 004 | Module 4 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp3 | Mod4 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB03KF002+U012UNA01UH131-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 13 | =G01NHB03HT004-BT02&EFS.001 | =G01NHB03&MFB.001 |  |  | U012UNA01UH131
=G01NHB03KF001 | G01NHB03KF001-BA01 | =G01NHB03KF001-BA01;XQ01 | ELY1 GRP3 CTRL U1 CELL VOLT1 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 CELL -VOLTAGE MODULE 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | XQ01 | Cell -Voltage Module 1 | Ely1 | Grp3 | CTRL U1 | Cell Volt1 | ANALOG1 | BA01 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB03KF001+U012UNA01UH132-KF02 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 01 | =G01NHB03KF001&EFS.053 | =G01NHB03&MFB.001 |  |  | U012UNA01UH132
=G01NHB03KF001 | G01NHB03KF001-BA02 | =G01NHB03KF001-BA02;XQ01 | ELY1 GRP3 CTRL U1 CELL VOLT2 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 2 CELL -VOLTAGE MODULE 2 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | KF | Control Units | 001 | Cell Voltage Measurement | -BA02 | Cell-Voltage-Measurement - Module 2 | XQ01 | Cell -Voltage Module 2 | Ely1 | Grp3 | CTRL U1 | Cell Volt2 | ANALOG1 | BA02 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB03KF001+U012UNA01UH132-KF02 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 02 | =G01NHB03KF001&EFS.053 | =G01NHB03&MFB.001 |  |  | U012UNA01UH132
=G01NHB03KF001 | G01NHB03KF001-BA03 | =G01NHB03KF001-BA03;XQ01 | ELY1 GRP3 CTRL U1 CELL VOLT3 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 3 CELL -VOLTAGE MODULE 3 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | KF | Control Units | 001 | Cell Voltage Measurement | -BA03 | Cell-Voltage-Measurement - Module 3 | XQ01 | Cell -Voltage Module 3 | Ely1 | Grp3 | CTRL U1 | Cell Volt3 | ANALOG1 | BA03 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB03KF001+U012UNA01UH132-KF03 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 01 | =G01NHB03KF001&EFS.053 | =G01NHB03&MFB.001 |  |  | U012UNA01UH132
=G01NHB03KF001 | G01NHB03KF001-BA04 | =G01NHB03KF001-BA04;XQ01 | ELY1 GRP3 CTRL U1 CELL VOLT4 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 4 CELL -VOLTAGE MODULE 4 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | KF | Control Units | 001 | Cell Voltage Measurement | -BA04 | Cell-Voltage-Measurement - Module 4 | XQ01 | Cell -Voltage Module 4 | Ely1 | Grp3 | CTRL U1 | Cell Volt4 | ANALOG1 | BA04 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB03KF001+U012UNA01UH132-KF03 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 02 | =G01NHB03KF001&EFS.053 | =G01NHB03&MFB.001 |  |  | U012UNA01UH132
=G01NHB04EQ001 | G01NHB04EQ001-BQ01 | =G01NHB04EQ001-BQ01;XQ01 | ELY1 GRP4 COOL QUAL1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ01 | Conductivity WP H2 | XQ01 | Analog process signal | Ely1 | Grp4 | Cool | Qual1 | ANALOG1 | -BQ01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | AI | 0 µS/cm | 20 µS/cm |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB04KF002+U012UNA01UH141-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | XQ01B | 01 | =G01NHB04EQ001-BQ01&EFS.001 | =G01NHB04&MFB.001 |  |  | U012UNA01UH141
=G01NHB04EQ001 | G01NHB04EQ001-BQ01 | =G01NHB04EQ001-BQ01;XQ02 | ELY1 GRP4 COOL QUAL1 ANALOG2 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ01 | Conductivity WP H2 | XQ02 | Analog process signal | Ely1 | Grp4 | Cool | Qual1 | ANALOG2 | -BQ01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | 0 µS/cm | 20 µS/cm | [7 empty] | AL |  | ASLL |  |  |  | =G01NHB04KF002+U012UNA01UH141-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ02 | XQ02B | 02 | =G01NHB04EQ001-BQ01&EFS.001 | =G01NHB04&MFB.001 |  |  | U012UNA01UH141
=G01NHB04EQ001 | G01NHB04EQ001-BQ02 | =G01NHB04EQ001-BQ02;XQ01 | ELY1 GRP4 COOL QUAL2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ02 | Conductivity WP O2 | XQ01 | Analog process signal | Ely1 | Grp4 | Cool | Qual2 | ANALOG1 | -BQ02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | AI | 0 µS/cm | 20 µS/cm |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB04KF002+U012UNA01UH141-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | XQ01B | 03 | =G01NHB04EQ001-BQ02&EFS.001 | =G01NHB04&MFB.001 |  |  | U012UNA01UH141
=G01NHB04EQ001 | G01NHB04EQ001-BQ02 | =G01NHB04EQ001-BQ02;XQ02 | ELY1 GRP4 COOL QUAL2 ANALOG2 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ02 | Conductivity WP O2 | XQ02 | Analog process signal | Ely1 | Grp4 | Cool | Qual2 | ANALOG2 | -BQ02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | 0 µS/cm | 20 µS/cm | [7 empty] | AL |  | ASLL |  |  |  | =G01NHB04KF002+U012UNA01UH141-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ02 | XQ02B | 04 | =G01NHB04EQ001-BQ02&EFS.001 | =G01NHB04&MFB.001 |  |  | U012UNA01UH141
=G01NHB04EQ001 | G01NHB04EQ001-BT01 | =G01NHB04EQ001-BT01;XQ01 | ELY1 GRP4 COOL TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 TEMPERATURE WCR ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BT01 | Temperature WCR | XQ01 | Analog process signal | Ely1 | Grp4 | Cool | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | -20 °C | 100 °C | [13 empty] | =G01NHB04KF002+U012UNA01UH141-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 05 | =G01NHB04EQ001-BT01&EFS.001 | =G01NHB04&MFB.001 |  |  | U012UNA01UH141
=G01NHB04EQ001 | G01NHB04EQ001-BT02 | =G01NHB04EQ001-BT02;XQ01 | ELY1 GRP4 COOL TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 TEMPERATURE WP H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BT02 | Temperature WP H2 | XQ01 | Analog process signal | Ely1 | Grp4 | Cool | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | TI | -20 °C | 100 °C | [5 empty] | AZH |  | AZL |  |  |  | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF05 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | XG02:1 | 1A | 01 | =G01NHB04EQ001-BT02&EFS.001 | =G01NHB04&MFB.001 |  |  | U012UNA01UH100
=G01NHB04EQ001 | G01NHB04EQ001-BT03 | =G01NHB04EQ001-BT03;XQ01 | ELY1 GRP4 COOL TEMP3 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 TEMPERATURE WP O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BT03 | Temperature WP O2 | XQ01 | Analog process signal | Ely1 | Grp4 | Cool | Temp3 | ANALOG1 | -BT03 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | TI | -20 °C | 100 °C | [5 empty] | AZH |  | AZL |  |  |  | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF05 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | XG02:3 | 3A | 02 | =G01NHB04EQ001-BT03&EFS.001 | =G01NHB04&MFB.001 |  |  | U012UNA01UH100
=G01NHB04EQ001 | G01NHB04EQ001-QN01 | =G01NHB04EQ001-QN01;XQ01 | ELY1 GRP4 COOL CV1 ANALOG1 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 COOLING WATER - CONTROL VALVE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -QN01 | Cooling Water - Control Valve | XQ01 | Analog process signal | Ely1 | Grp4 | Cool | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | G | [15 empty] | =G01NHB04KF002+U012UNA01UH141-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 14 | =G01NHB04EQ001-QN01&EFS.001 | =G01NHB04&MFB.001 |  |  | U012UNA01UH141
=G01NHB04HT001 | G01NHB04HT001-BT01 | =G01NHB04HT001-BT01;XQ01 | ELY1 GRP4 MOD1 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 ELECTROLYSIS MODULES MODULE 1 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | HT | Electrolysis Modules | 001 | Module 1 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp4 | Mod1 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB04KF002+U012UNA01UH141-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 06 | =G01NHB04HT001-BT01&EFS.001 | =G01NHB04&MFB.001 |  |  | U012UNA01UH141
=G01NHB04HT001 | G01NHB04HT001-BT02 | =G01NHB04HT001-BT02;XQ01 | ELY1 GRP4 MOD1 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 ELECTROLYSIS MODULES MODULE 1 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | HT | Electrolysis Modules | 001 | Module 1 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp4 | Mod1 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB04KF002+U012UNA01UH141-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 07 | =G01NHB04HT001-BT02&EFS.001 | =G01NHB04&MFB.001 |  |  | U012UNA01UH141
=G01NHB04HT002 | G01NHB04HT002-BT01 | =G01NHB04HT002-BT01;XQ01 | ELY1 GRP4 MOD2 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 ELECTROLYSIS MODULES MODULE 2 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | HT | Electrolysis Modules | 002 | Module 2 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp4 | Mod2 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB04KF002+U012UNA01UH141-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 08 | =G01NHB04HT002-BT01&EFS.001 | =G01NHB04&MFB.001 |  |  | U012UNA01UH141
=G01NHB04HT002 | G01NHB04HT002-BT02 | =G01NHB04HT002-BT02;XQ01 | ELY1 GRP4 MOD2 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 ELECTROLYSIS MODULES MODULE 2 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | HT | Electrolysis Modules | 002 | Module 2 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp4 | Mod2 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB04KF002+U012UNA01UH141-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 09 | =G01NHB04HT002-BT02&EFS.001 | =G01NHB04&MFB.001 |  |  | U012UNA01UH141
=G01NHB04HT003 | G01NHB04HT003-BT01 | =G01NHB04HT003-BT01;XQ01 | ELY1 GRP4 MOD3 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 ELECTROLYSIS MODULES MODULE 3 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | HT | Electrolysis Modules | 003 | Module 3 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp4 | Mod3 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB04KF002+U012UNA01UH141-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 10 | =G01NHB04HT003-BT01&EFS.001 | =G01NHB04&MFB.001 |  |  | U012UNA01UH141
=G01NHB04HT003 | G01NHB04HT003-BT02 | =G01NHB04HT003-BT02;XQ01 | ELY1 GRP4 MOD3 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 ELECTROLYSIS MODULES MODULE 3 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | HT | Electrolysis Modules | 003 | Module 3 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp4 | Mod3 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB04KF002+U012UNA01UH141-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 11 | =G01NHB04HT003-BT02&EFS.001 | =G01NHB04&MFB.001 |  |  | U012UNA01UH141
=G01NHB04HT004 | G01NHB04HT004-BT01 | =G01NHB04HT004-BT01;XQ01 | ELY1 GRP4 MOD4 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 ELECTROLYSIS MODULES MODULE 4 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | HT | Electrolysis Modules | 004 | Module 4 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp4 | Mod4 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB04KF002+U012UNA01UH141-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 12 | =G01NHB04HT004-BT01&EFS.001 | =G01NHB04&MFB.001 |  |  | U012UNA01UH141
=G01NHB04HT004 | G01NHB04HT004-BT02 | =G01NHB04HT004-BT02;XQ01 | ELY1 GRP4 MOD4 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 ELECTROLYSIS MODULES MODULE 4 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | HT | Electrolysis Modules | 004 | Module 4 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp4 | Mod4 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB04KF002+U012UNA01UH141-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 13 | =G01NHB04HT004-BT02&EFS.001 | =G01NHB04&MFB.001 |  |  | U012UNA01UH141
=G01NHB04KF001 | G01NHB04KF001-BA01 | =G01NHB04KF001-BA01;XQ01 | ELY1 GRP4 CTRL U1 CELL VOLT1 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 CELL -VOLTAGE MODULE 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | XQ01 | Cell -Voltage Module 1 | Ely1 | Grp4 | CTRL U1 | Cell Volt1 | ANALOG1 | BA01 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB04KF001+U012UNA01UH142-KF02 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 01 | =G01NHB04KF001&EFS.053 | =G01NHB04&MFB.001 |  |  | U012UNA01UH142
=G01NHB04KF001 | G01NHB04KF001-BA02 | =G01NHB04KF001-BA02;XQ01 | ELY1 GRP4 CTRL U1 CELL VOLT2 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 2 CELL -VOLTAGE MODULE 2 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | KF | Control Units | 001 | Cell Voltage Measurement | -BA02 | Cell-Voltage-Measurement - Module 2 | XQ01 | Cell -Voltage Module 2 | Ely1 | Grp4 | CTRL U1 | Cell Volt2 | ANALOG1 | BA02 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB04KF001+U012UNA01UH142-KF02 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 02 | =G01NHB04KF001&EFS.053 | =G01NHB04&MFB.001 |  |  | U012UNA01UH142
=G01NHB04KF001 | G01NHB04KF001-BA03 | =G01NHB04KF001-BA03;XQ01 | ELY1 GRP4 CTRL U1 CELL VOLT3 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 3 CELL -VOLTAGE MODULE 3 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | KF | Control Units | 001 | Cell Voltage Measurement | -BA03 | Cell-Voltage-Measurement - Module 3 | XQ01 | Cell -Voltage Module 3 | Ely1 | Grp4 | CTRL U1 | Cell Volt3 | ANALOG1 | BA03 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB04KF001+U012UNA01UH142-KF03 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 01 | =G01NHB04KF001&EFS.053 | =G01NHB04&MFB.001 |  |  | U012UNA01UH142
=G01NHB04KF001 | G01NHB04KF001-BA04 | =G01NHB04KF001-BA04;XQ01 | ELY1 GRP4 CTRL U1 CELL VOLT4 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 4 CELL -VOLTAGE MODULE 4 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | KF | Control Units | 001 | Cell Voltage Measurement | -BA04 | Cell-Voltage-Measurement - Module 4 | XQ01 | Cell -Voltage Module 4 | Ely1 | Grp4 | CTRL U1 | Cell Volt4 | ANALOG1 | BA04 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB04KF001+U012UNA01UH142-KF03 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 02 | =G01NHB04KF001&EFS.053 | =G01NHB04&MFB.001 |  |  | U012UNA01UH142
=G01NHB05EQ001 | G01NHB05EQ001-BQ01 | =G01NHB05EQ001-BQ01;XQ01 | ELY1 GRP5 COOL QUAL1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ01 | Conductivity WP H2 | XQ01 | Analog process signal | Ely1 | Grp5 | Cool | Qual1 | ANALOG1 | -BQ01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | AI | 0 µS/cm | 20 µS/cm |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB05KF002+U012UNA01UH151-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | XQ01B | 01 | =G01NHB05EQ001-BQ01&EFS.001 | =G01NHB05&MFB.001 |  |  | U012UNA01UH151
=G01NHB05EQ001 | G01NHB05EQ001-BQ01 | =G01NHB05EQ001-BQ01;XQ02 | ELY1 GRP5 COOL QUAL1 ANALOG2 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ01 | Conductivity WP H2 | XQ02 | Analog process signal | Ely1 | Grp5 | Cool | Qual1 | ANALOG2 | -BQ01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | 0 µS/cm | 20 µS/cm | [7 empty] | AL |  | ASLL |  |  |  | =G01NHB05KF002+U012UNA01UH151-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ02 | XQ02B | 02 | =G01NHB05EQ001-BQ01&EFS.001 | =G01NHB05&MFB.001 |  |  | U012UNA01UH151
=G01NHB05EQ001 | G01NHB05EQ001-BQ02 | =G01NHB05EQ001-BQ02;XQ01 | ELY1 GRP5 COOL QUAL2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ02 | Conductivity WP O2 | XQ01 | Analog process signal | Ely1 | Grp5 | Cool | Qual2 | ANALOG1 | -BQ02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | AI | 0 µS/cm | 20 µS/cm |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB05KF002+U012UNA01UH151-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | XQ01B | 03 | =G01NHB05EQ001-BQ02&EFS.001 | =G01NHB05&MFB.001 |  |  | U012UNA01UH151
=G01NHB05EQ001 | G01NHB05EQ001-BQ02 | =G01NHB05EQ001-BQ02;XQ02 | ELY1 GRP5 COOL QUAL2 ANALOG2 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ02 | Conductivity WP O2 | XQ02 | Analog process signal | Ely1 | Grp5 | Cool | Qual2 | ANALOG2 | -BQ02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | 0 µS/cm | 20 µS/cm | [7 empty] | AL |  | ASLL |  |  |  | =G01NHB05KF002+U012UNA01UH151-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ02 | XQ02B | 04 | =G01NHB05EQ001-BQ02&EFS.001 | =G01NHB05&MFB.001 |  |  | U012UNA01UH151
=G01NHB05EQ001 | G01NHB05EQ001-BT01 | =G01NHB05EQ001-BT01;XQ01 | ELY1 GRP5 COOL TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 TEMPERATURE WCR ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BT01 | Temperature WCR | XQ01 | Analog process signal | Ely1 | Grp5 | Cool | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | -20 °C | 100 °C | [13 empty] | =G01NHB05KF002+U012UNA01UH151-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 05 | =G01NHB05EQ001-BT01&EFS.001 | =G01NHB05&MFB.001 |  |  | U012UNA01UH151
=G01NHB05EQ001 | G01NHB05EQ001-BT02 | =G01NHB05EQ001-BT02;XQ01 | ELY1 GRP5 COOL TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 TEMPERATURE WP H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BT02 | Temperature WP H2 | XQ01 | Analog process signal | Ely1 | Grp5 | Cool | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | TI | -20 °C | 100 °C | [5 empty] | AZH |  | AZL |  |  |  | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF05 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | XG02:1 | 1A | 03 | =G01NHB05EQ001-BT02&EFS.001 | =G01NHB05&MFB.001 |  |  | U012UNA01UH100
=G01NHB05EQ001 | G01NHB05EQ001-BT03 | =G01NHB05EQ001-BT03;XQ01 | ELY1 GRP5 COOL TEMP3 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 TEMPERATURE WP O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BT03 | Temperature WP O2 | XQ01 | Analog process signal | Ely1 | Grp5 | Cool | Temp3 | ANALOG1 | -BT03 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | TI | -20 °C | 100 °C | [5 empty] | AZH |  | AZL |  |  |  | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF05 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | XG02:3 | 3A | 04 | =G01NHB05EQ001-BT03&EFS.001 | =G01NHB05&MFB.001 |  |  | U012UNA01UH100
=G01NHB05EQ001 | G01NHB05EQ001-QN01 | =G01NHB05EQ001-QN01;XQ01 | ELY1 GRP5 COOL CV1 ANALOG1 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 COOLING WATER - CONTROL VALVE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -QN01 | Cooling Water - Control Valve | XQ01 | Analog process signal | Ely1 | Grp5 | Cool | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | G | [15 empty] | =G01NHB05KF002+U012UNA01UH151-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 14 | =G01NHB05EQ001-QN01&EFS.001 | =G01NHB05&MFB.001 |  |  | U012UNA01UH151
=G01NHB05HT001 | G01NHB05HT001-BT01 | =G01NHB05HT001-BT01;XQ01 | ELY1 GRP5 MOD1 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 ELECTROLYSIS MODULES MODULE 1 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | HT | Electrolysis Modules | 001 | Module 1 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp5 | Mod1 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB05KF002+U012UNA01UH151-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 06 | =G01NHB05HT001-BT01&EFS.001 | =G01NHB05&MFB.001 |  |  | U012UNA01UH151
=G01NHB05HT001 | G01NHB05HT001-BT02 | =G01NHB05HT001-BT02;XQ01 | ELY1 GRP5 MOD1 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 ELECTROLYSIS MODULES MODULE 1 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | HT | Electrolysis Modules | 001 | Module 1 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp5 | Mod1 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB05KF002+U012UNA01UH151-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 07 | =G01NHB05HT001-BT02&EFS.001 | =G01NHB05&MFB.001 |  |  | U012UNA01UH151
=G01NHB05HT002 | G01NHB05HT002-BT01 | =G01NHB05HT002-BT01;XQ01 | ELY1 GRP5 MOD2 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 ELECTROLYSIS MODULES MODULE 2 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | HT | Electrolysis Modules | 002 | Module 2 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp5 | Mod2 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB05KF002+U012UNA01UH151-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 08 | =G01NHB05HT002-BT01&EFS.001 | =G01NHB05&MFB.001 |  |  | U012UNA01UH151
=G01NHB05HT002 | G01NHB05HT002-BT02 | =G01NHB05HT002-BT02;XQ01 | ELY1 GRP5 MOD2 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 ELECTROLYSIS MODULES MODULE 2 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | HT | Electrolysis Modules | 002 | Module 2 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp5 | Mod2 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB05KF002+U012UNA01UH151-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 09 | =G01NHB05HT002-BT02&EFS.001 | =G01NHB05&MFB.001 |  |  | U012UNA01UH151
=G01NHB05HT003 | G01NHB05HT003-BT01 | =G01NHB05HT003-BT01;XQ01 | ELY1 GRP5 MOD3 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 ELECTROLYSIS MODULES MODULE 3 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | HT | Electrolysis Modules | 003 | Module 3 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp5 | Mod3 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB05KF002+U012UNA01UH151-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 10 | =G01NHB05HT003-BT01&EFS.001 | =G01NHB05&MFB.001 |  |  | U012UNA01UH151
=G01NHB05HT003 | G01NHB05HT003-BT02 | =G01NHB05HT003-BT02;XQ01 | ELY1 GRP5 MOD3 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 ELECTROLYSIS MODULES MODULE 3 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | HT | Electrolysis Modules | 003 | Module 3 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp5 | Mod3 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB05KF002+U012UNA01UH151-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 11 | =G01NHB05HT003-BT02&EFS.001 | =G01NHB05&MFB.001 |  |  | U012UNA01UH151
=G01NHB05HT004 | G01NHB05HT004-BT01 | =G01NHB05HT004-BT01;XQ01 | ELY1 GRP5 MOD4 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 ELECTROLYSIS MODULES MODULE 4 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | HT | Electrolysis Modules | 004 | Module 4 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp5 | Mod4 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB05KF002+U012UNA01UH151-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 12 | =G01NHB05HT004-BT01&EFS.001 | =G01NHB05&MFB.001 |  |  | U012UNA01UH151
=G01NHB05HT004 | G01NHB05HT004-BT02 | =G01NHB05HT004-BT02;XQ01 | ELY1 GRP5 MOD4 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 ELECTROLYSIS MODULES MODULE 4 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | HT | Electrolysis Modules | 004 | Module 4 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp5 | Mod4 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB05KF002+U012UNA01UH151-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 13 | =G01NHB05HT004-BT02&EFS.001 | =G01NHB05&MFB.001 |  |  | U012UNA01UH151
=G01NHB05KF001 | G01NHB05KF001-BA01 | =G01NHB05KF001-BA01;XQ01 | ELY1 GRP5 CTRL U1 CELL VOLT1 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 CELL -VOLTAGE MODULE 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | XQ01 | Cell -Voltage Module 1 | Ely1 | Grp5 | CTRL U1 | Cell Volt1 | ANALOG1 | BA01 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB05KF001+U012UNA01UH152-KF02 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 01 | =G01NHB05KF001&EFS.053 | =G01NHB05&MFB.001 |  |  | U012UNA01UH152
=G01NHB05KF001 | G01NHB05KF001-BA02 | =G01NHB05KF001-BA02;XQ01 | ELY1 GRP5 CTRL U1 CELL VOLT2 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 2 CELL -VOLTAGE MODULE 2 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | KF | Control Units | 001 | Cell Voltage Measurement | -BA02 | Cell-Voltage-Measurement - Module 2 | XQ01 | Cell -Voltage Module 2 | Ely1 | Grp5 | CTRL U1 | Cell Volt2 | ANALOG1 | BA02 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB05KF001+U012UNA01UH152-KF02 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 02 | =G01NHB05KF001&EFS.053 | =G01NHB05&MFB.001 |  |  | U012UNA01UH152
=G01NHB05KF001 | G01NHB05KF001-BA03 | =G01NHB05KF001-BA03;XQ01 | ELY1 GRP5 CTRL U1 CELL VOLT3 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 3 CELL -VOLTAGE MODULE 3 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | KF | Control Units | 001 | Cell Voltage Measurement | -BA03 | Cell-Voltage-Measurement - Module 3 | XQ01 | Cell -Voltage Module 3 | Ely1 | Grp5 | CTRL U1 | Cell Volt3 | ANALOG1 | BA03 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB05KF001+U012UNA01UH152-KF03 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 01 | =G01NHB05KF001&EFS.053 | =G01NHB05&MFB.001 |  |  | U012UNA01UH152
=G01NHB05KF001 | G01NHB05KF001-BA04 | =G01NHB05KF001-BA04;XQ01 | ELY1 GRP5 CTRL U1 CELL VOLT4 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 4 CELL -VOLTAGE MODULE 4 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | KF | Control Units | 001 | Cell Voltage Measurement | -BA04 | Cell-Voltage-Measurement - Module 4 | XQ01 | Cell -Voltage Module 4 | Ely1 | Grp5 | CTRL U1 | Cell Volt4 | ANALOG1 | BA04 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB05KF001+U012UNA01UH152-KF03 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 02 | =G01NHB05KF001&EFS.053 | =G01NHB05&MFB.001 |  |  | U012UNA01UH152
=G01NHB06EQ001 | G01NHB06EQ001-BQ01 | =G01NHB06EQ001-BQ01;XQ01 | ELY1 GRP6 COOL QUAL1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ01 | Conductivity WP H2 | XQ01 | Analog process signal | Ely1 | Grp6 | Cool | Qual1 | ANALOG1 | -BQ01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | AI | 0 µS/cm | 20 µS/cm |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB06KF002+U012UNA01UH161-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | XQ01B | 01 | =G01NHB06EQ001-BQ01&EFS.001 | =G01NHB06&MFB.001 |  |  | U012UNA01UH161
=G01NHB06EQ001 | G01NHB06EQ001-BQ01 | =G01NHB06EQ001-BQ01;XQ02 | ELY1 GRP6 COOL QUAL1 ANALOG2 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ01 | Conductivity WP H2 | XQ02 | Analog process signal | Ely1 | Grp6 | Cool | Qual1 | ANALOG2 | -BQ01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | 0 µS/cm | 20 µS/cm | [7 empty] | AL |  | ASLL |  |  |  | =G01NHB06KF002+U012UNA01UH161-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ02 | XQ02B | 02 | =G01NHB06EQ001-BQ01&EFS.001 | =G01NHB06&MFB.001 |  |  | U012UNA01UH161
=G01NHB06EQ001 | G01NHB06EQ001-BQ02 | =G01NHB06EQ001-BQ02;XQ01 | ELY1 GRP6 COOL QUAL2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ02 | Conductivity WP O2 | XQ01 | Analog process signal | Ely1 | Grp6 | Cool | Qual2 | ANALOG1 | -BQ02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | AI | 0 µS/cm | 20 µS/cm |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB06KF002+U012UNA01UH161-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | XQ01B | 03 | =G01NHB06EQ001-BQ02&EFS.001 | =G01NHB06&MFB.001 |  |  | U012UNA01UH161
=G01NHB06EQ001 | G01NHB06EQ001-BQ02 | =G01NHB06EQ001-BQ02;XQ02 | ELY1 GRP6 COOL QUAL2 ANALOG2 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 CONDUCTIVITY WP O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BQ02 | Conductivity WP O2 | XQ02 | Analog process signal | Ely1 | Grp6 | Cool | Qual2 | ANALOG2 | -BQ02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | 0 µS/cm | 20 µS/cm | [7 empty] | AL |  | ASLL |  |  |  | =G01NHB06KF002+U012UNA01UH161-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ02 | XQ02B | 04 | =G01NHB06EQ001-BQ02&EFS.001 | =G01NHB06&MFB.001 |  |  | U012UNA01UH161
=G01NHB06EQ001 | G01NHB06EQ001-BT01 | =G01NHB06EQ001-BT01;XQ01 | ELY1 GRP6 COOL TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 TEMPERATURE WCR ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BT01 | Temperature WCR | XQ01 | Analog process signal | Ely1 | Grp6 | Cool | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | -20 °C | 100 °C | [13 empty] | =G01NHB06KF002+U012UNA01UH161-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 05 | =G01NHB06EQ001-BT01&EFS.001 | =G01NHB06&MFB.001 |  |  | U012UNA01UH161
=G01NHB06EQ001 | G01NHB06EQ001-BT02 | =G01NHB06EQ001-BT02;XQ01 | ELY1 GRP6 COOL TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 TEMPERATURE WP H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BT02 | Temperature WP H2 | XQ01 | Analog process signal | Ely1 | Grp6 | Cool | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | TI | -20 °C | 100 °C | [5 empty] | AZH |  | AZL |  |  |  | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF05 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | XG02:1 | 1A | 05 | =G01NHB06EQ001-BT02&EFS.001 | =G01NHB06&MFB.001 |  |  | U012UNA01UH100
=G01NHB06EQ001 | G01NHB06EQ001-BT03 | =G01NHB06EQ001-BT03;XQ01 | ELY1 GRP6 COOL TEMP3 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 TEMPERATURE WP O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -BT03 | Temperature WP O2 | XQ01 | Analog process signal | Ely1 | Grp6 | Cool | Temp3 | ANALOG1 | -BT03 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | TI | -20 °C | 100 °C | [5 empty] | AZH |  | AZL |  |  |  | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF05 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | XG02:3 | 3A | 06 | =G01NHB06EQ001-BT03&EFS.001 | =G01NHB06&MFB.001 |  |  | U012UNA01UH100
=G01NHB06EQ001 | G01NHB06EQ001-QN01 | =G01NHB06EQ001-QN01;XQ01 | ELY1 GRP6 COOL CV1 ANALOG1 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 COOLING WATER - CONTROL VALVE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -QN01 | Cooling Water - Control Valve | XQ01 | Analog process signal | Ely1 | Grp6 | Cool | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | G | [15 empty] | =G01NHB06KF002+U012UNA01UH161-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 14 | =G01NHB06EQ001-QN01&EFS.001 | =G01NHB06&MFB.001 |  |  | U012UNA01UH161
=G01NHB06HT001 | G01NHB06HT001-BT01 | =G01NHB06HT001-BT01;XQ01 | ELY1 GRP6 MOD1 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 ELECTROLYSIS MODULES MODULE 1 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | HT | Electrolysis Modules | 001 | Module 1 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp6 | Mod1 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB06KF002+U012UNA01UH161-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 06 | =G01NHB06HT001-BT01&EFS.001 | =G01NHB06&MFB.001 |  |  | U012UNA01UH161
=G01NHB06HT001 | G01NHB06HT001-BT02 | =G01NHB06HT001-BT02;XQ01 | ELY1 GRP6 MOD1 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 ELECTROLYSIS MODULES MODULE 1 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | HT | Electrolysis Modules | 001 | Module 1 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp6 | Mod1 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB06KF002+U012UNA01UH161-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 07 | =G01NHB06HT001-BT02&EFS.001 | =G01NHB06&MFB.001 |  |  | U012UNA01UH161
=G01NHB06HT002 | G01NHB06HT002-BT01 | =G01NHB06HT002-BT01;XQ01 | ELY1 GRP6 MOD2 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 ELECTROLYSIS MODULES MODULE 2 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | HT | Electrolysis Modules | 002 | Module 2 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp6 | Mod2 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB06KF002+U012UNA01UH161-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 08 | =G01NHB06HT002-BT01&EFS.001 | =G01NHB06&MFB.001 |  |  | U012UNA01UH161
=G01NHB06HT002 | G01NHB06HT002-BT02 | =G01NHB06HT002-BT02;XQ01 | ELY1 GRP6 MOD2 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 ELECTROLYSIS MODULES MODULE 2 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | HT | Electrolysis Modules | 002 | Module 2 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp6 | Mod2 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB06KF002+U012UNA01UH161-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 09 | =G01NHB06HT002-BT02&EFS.001 | =G01NHB06&MFB.001 |  |  | U012UNA01UH161
=G01NHB06HT003 | G01NHB06HT003-BT01 | =G01NHB06HT003-BT01;XQ01 | ELY1 GRP6 MOD3 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 ELECTROLYSIS MODULES MODULE 3 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | HT | Electrolysis Modules | 003 | Module 3 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp6 | Mod3 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB06KF002+U012UNA01UH161-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 10 | =G01NHB06HT003-BT01&EFS.001 | =G01NHB06&MFB.001 |  |  | U012UNA01UH161
=G01NHB06HT003 | G01NHB06HT003-BT02 | =G01NHB06HT003-BT02;XQ01 | ELY1 GRP6 MOD3 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 ELECTROLYSIS MODULES MODULE 3 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | HT | Electrolysis Modules | 003 | Module 3 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp6 | Mod3 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB06KF002+U012UNA01UH161-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 11 | =G01NHB06HT003-BT02&EFS.001 | =G01NHB06&MFB.001 |  |  | U012UNA01UH161
=G01NHB06HT004 | G01NHB06HT004-BT01 | =G01NHB06HT004-BT01;XQ01 | ELY1 GRP6 MOD4 TEMP1 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 ELECTROLYSIS MODULES MODULE 4 TEMPERATURE MODULE OUTLET O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | HT | Electrolysis Modules | 004 | Module 4 | -BT01 | Temperature Module Outlet O2 | XQ01 | Analog process signal | Ely1 | Grp6 | Mod4 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB06KF002+U012UNA01UH161-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 12 | =G01NHB06HT004-BT01&EFS.001 | =G01NHB06&MFB.001 |  |  | U012UNA01UH161
=G01NHB06HT004 | G01NHB06HT004-BT02 | =G01NHB06HT004-BT02;XQ01 | ELY1 GRP6 MOD4 TEMP2 ANALOG1 | 28 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 ELECTROLYSIS MODULES MODULE 4 TEMPERATURE MODULE OUTLET H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | HT | Electrolysis Modules | 004 | Module 4 | -BT02 | Temperature Module Outlet H2 | XQ01 | Analog process signal | Ely1 | Grp6 | Mod4 | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C |  |  |  | ASHH |  | AH | [7 empty] | =G01NHB06KF002+U012UNA01UH161-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 13 | =G01NHB06HT004-BT02&EFS.001 | =G01NHB06&MFB.001 |  |  | U012UNA01UH161
=G01NHB06KF001 | G01NHB06KF001-BA01 | =G01NHB06KF001-BA01;XQ01 | ELY1 GRP6 CTRL U1 CELL VOLT1 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 CELL -VOLTAGE MODULE 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | XQ01 | Cell -Voltage Module 1 | Ely1 | Grp6 | CTRL U1 | Cell Volt1 | ANALOG1 | BA01 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB06KF001+U012UNA01UH162-KF02 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 01 | =G01NHB06KF001&EFS.053 | =G01NHB06&MFB.001 |  |  | U012UNA01UH162
=G01NHB06KF001 | G01NHB06KF001-BA02 | =G01NHB06KF001-BA02;XQ01 | ELY1 GRP6 CTRL U1 CELL VOLT2 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 2 CELL -VOLTAGE MODULE 2 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | KF | Control Units | 001 | Cell Voltage Measurement | -BA02 | Cell-Voltage-Measurement - Module 2 | XQ01 | Cell -Voltage Module 2 | Ely1 | Grp6 | CTRL U1 | Cell Volt2 | ANALOG1 | BA02 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB06KF001+U012UNA01UH162-KF02 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 02 | =G01NHB06KF001&EFS.053 | =G01NHB06&MFB.001 |  |  | U012UNA01UH162
=G01NHB06KF001 | G01NHB06KF001-BA03 | =G01NHB06KF001-BA03;XQ01 | ELY1 GRP6 CTRL U1 CELL VOLT3 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 3 CELL -VOLTAGE MODULE 3 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | KF | Control Units | 001 | Cell Voltage Measurement | -BA03 | Cell-Voltage-Measurement - Module 3 | XQ01 | Cell -Voltage Module 3 | Ely1 | Grp6 | CTRL U1 | Cell Volt3 | ANALOG1 | BA03 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB06KF001+U012UNA01UH162-KF03 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 01 | =G01NHB06KF001&EFS.053 | =G01NHB06&MFB.001 |  |  | U012UNA01UH162
=G01NHB06KF001 | G01NHB06KF001-BA04 | =G01NHB06KF001-BA04;XQ01 | ELY1 GRP6 CTRL U1 CELL VOLT4 ANALOG1 | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 4 CELL -VOLTAGE MODULE 4 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | KF | Control Units | 001 | Cell Voltage Measurement | -BA04 | Cell-Voltage-Measurement - Module 4 | XQ01 | Cell -Voltage Module 4 | Ely1 | Grp6 | CTRL U1 | Cell Volt4 | ANALOG1 | BA04 | Electrical | 0...10V | 0...10V | Field bus | Undefined |  |  | AI | 0 | EIC | 0 V | 3 V |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB06KF001+U012UNA01UH162-KF03 | 6ES7 134-6HB00-0CA1, AI 2 X U/I 2-, 4-WIRE HF |  |  | 02 | =G01NHB06KF001&EFS.053 | =G01NHB06&MFB.001 |  |  | U012UNA01UH162
=G01NHC01BL001 | G01NHC01BL001-BL01 | =G01NHC01BL001-BL01;XQ01 | ELY1 H2 TRT LVL MEAS LVL1 ANALOG1 | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM LEVEL MEASUREMENT SYSTEM LEVEL MEASUREMENT SYSTEM 1 H2 WATER LEVEL MEASUREMENT ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BL | Level Measurement System | 001 | Level Measurement System 1 | -BL01 | H2 Water Level Measurement | XQ01 | Analog process signal | Ely1 | H2 TRT | Lvl Meas | Lvl1 | ANALOG1 | -BL01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | LI | 0 mm | 1000 mm | [11 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF06 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | B10:XQ01 | XQ01B | 01 | =G01NHC01BL001-BL01&EFS.001 | =G01NHC01&MFB.001 |  |  | U012UNA01UH100
=G01NHC01BL001 | G01NHC01BL001-BL02 | =G01NHC01BL001-BL02;XQ01 | ELY1 H2 TRT LVL MEAS LVL2 ANALOG1 | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM LEVEL MEASUREMENT SYSTEM LEVEL MEASUREMENT SYSTEM 1 H2 WATER LEVEL MEASUREMENT ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BL | Level Measurement System | 001 | Level Measurement System 1 | -BL02 | H2 Water Level Measurement | XQ01 | Analog process signal | Ely1 | H2 TRT | Lvl Meas | Lvl2 | ANALOG1 | -BL02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | LIC | 0 mm | 1000 mm |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  | No |  | =G01NHY01KF001+U012UNA01UH100-KF11 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 15 | =G01NHC01BL001-BL02&EFS.001 | =G01NHC01&MFB.001 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-BF01 | =G01NHC01BQ001-BF01;XG01 | ELY1 H2 TRT QUAL FLOW1 CB ON/OPN/MAX1 | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM 10301; FLOWMETER GENERAL CHECK BACK ON/OPEN // LIMIT VALUE >MAX 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -BF01 | 10301; Flowmeter general | XG01 | Check back on/open // Limit value >max 1 | Ely1 | H2 TRT | QUAL | Flow1 | CB ON/OPN/MAX1 | -BF01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | FSZ | [7 empty] | AH |  | AL |  |  |  | Yes |  | =G01NHY01KF001+U012UNA01UH100-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XG01 | EA01 | 03 | =G01NHC01BQ001-BF01&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-BF02 | =G01NHC01BQ001-BF02;XG02 | ELY1 H2 TRT QUAL FLOW2 CB ON/OPN/MIN1 | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM 10301; FLOWMETER GENERAL CHECK BACK OFF/CLOSED // LIMIT VALUE >MIN 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -BF02 | 10301; Flowmeter general | XG02 | Check back off/closed // Limit value >min 1 | Ely1 | H2 TRT | QUAL | Flow2 | CB ON/OPN/MIN1 | -BF02 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | FSZ | [7 empty] | AH |  | AL |  |  |  | Yes |  | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:5 | 5B | 13 | =G01NHC01BQ001-BF02&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01GT001 | G01NHC01GT001-BT01 | =G01NHC01GT001-BT01;XQ01 | ELY1 H2 TRT LEAD OFF TEMP1 ANALOG1 | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM GAS LEAD OFF SYSTEMS GAS LEAD OFF SYSTEM 1 TEMPERATURE GAS COOLER H2 OUTLET ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | GT | Gas Lead off Systems | 001 | Gas Lead off System 1 | -BT01 | Temperature Gas Cooler H2 Outlet | XQ01 | Analog process signal | Ely1 | H2 TRT | Lead Off | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C | [5 empty] | AH | [7 empty] | =G01NHY01KF001+U012UNA01UH100-KF12 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 07 | =G01NHC01GT001-BT01&EFS.001 | =G01NHC01&MFB.002 |  |  | U012UNA01UH100
=G01NHC01GT001 | G01NHC01GT001-QN01 | =G01NHC01GT001-QN01;XQ01 | ELY1 H2 TRT LEAD OFF CV1 ANALOG1 | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM GAS LEAD OFF SYSTEMS GAS LEAD OFF SYSTEM 1 CONTROL VALVE - H2 PRODUCT ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | GT | Gas Lead off Systems | 001 | Gas Lead off System 1 | -QN01 | Control valve - H2 Product | XQ01 | Analog process signal | Ely1 | H2 TRT | Lead Off | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF12 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 13 | =G01NHC01GT001-QN01&EFS.001 | =G01NHC01&MFB.002 |  |  | U012UNA01UH100
=G01NHC01GT001 | G01NHC01GT001-QN02 | =G01NHC01GT001-QN02;XQ01 | ELY1 H2 TRT LEAD OFF CV2 ANALOG1 | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM GAS LEAD OFF SYSTEMS GAS LEAD OFF SYSTEM 1 CONTROL VALVE - H2 BLOW OFF ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | GT | Gas Lead off Systems | 001 | Gas Lead off System 1 | -QN02 | Control valve - H2 Blow off | XQ01 | Analog process signal | Ely1 | H2 TRT | Lead Off | CV2 | ANALOG1 | -QN02KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF13 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 09 | =G01NHC01GT001-QN02&EFS.001 | =G01NHC01&MFB.002 |  |  | U012UNA01UH100
=G01NHC01HP001 | G01NHC01HP001-BP01 | =G01NHC01HP001-BP01;XQ01 | ELY1 H2 TRT SYS 1 PRES1 ANALOG1 | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM GAS COOLING SYSTEMS GAS COOLING SYSTEM 1 PRESSURE - H2 HEADER ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | HP | Gas Cooling Systems | 001 | Gas Cooling System 1 | -BP01 | Pressure - H2 Header | XQ01 | Analog process signal | Ely1 | H2 TRT | SYS 1 | Pres1 | ANALOG1 | -BP01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | PI | -25 mbar | 225 mbar | [9 empty] | AZLL |  | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF06 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | B10:XQ01 | XQ01 | 04 | =G01NHC01HP001-BP01&EFS.001 | =G01NHC01&MFB.001 |  |  | U012UNA01UH100
=G01NHC01HP001 | G01NHC01HP001-BP02 | =G01NHC01HP001-BP02;XQ01 | ELY1 H2 TRT SYS 1 PRES2 ANALOG1 | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM GAS COOLING SYSTEMS GAS COOLING SYSTEM 1 PRESSURE - H2 HEADER ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | HP | Gas Cooling Systems | 001 | Gas Cooling System 1 | -BP02 | Pressure - H2 Header | XQ01 | Analog process signal | Ely1 | H2 TRT | SYS 1 | Pres2 | ANALOG1 | -BP02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | PIC | -25 mbar | 225 mbar |  |  |  | ASHH |  | AH |  | ASL | [5 empty] | =G01NHY01KF001+U012UNA01UH100-KF11 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 16 | =G01NHC01HP001-BP02&EFS.001 | =G01NHC01&MFB.001 |  |  | U012UNA01UH100
=G01NHC01HP001 | G01NHC01HP001-BT01 | =G01NHC01HP001-BT01;XQ01 | ELY1 H2 TRT SYS 1 TEMP1 ANALOG1 | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM GAS COOLING SYSTEMS GAS COOLING SYSTEM 1 TEMPERATURE GAS COOLER H2 INLET ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | HP | Gas Cooling Systems | 001 | Gas Cooling System 1 | -BT01 | Temperature Gas Cooler H2 Inlet | XQ01 | Analog process signal | Ely1 | H2 TRT | SYS 1 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | -20 °C | 100 °C | [13 empty] | =G01NHY01KF001+U012UNA01UH100-KF12 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 05 | =G01NHC01HP001-BT01&EFS.001 | =G01NHC01&MFB.002 |  |  | U012UNA01UH100
=G01NHE01BL001 | G01NHE01BL001-BL01 | =G01NHE01BL001-BL01;XQ01 | ELY1 O2 TRT LVL MEAS LVL1 ANALOG1 | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM LEVEL MEASUREMENT SYSTEM LEVEL MEASUREMENT SYSTEM 1 O2 WATER LEVEL MEASUREMENT ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BL | Level Measurement System | 001 | Level Measurement System 1 | -BL01 | O2 Water Level Measurement | XQ01 | Analog process signal | Ely1 | O2 TRT | Lvl Meas | Lvl1 | ANALOG1 | -BL01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | LI | 0 mm | 1000 mm | [11 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF06 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | B10:XQ01 | XQ01 | 05 | =G01NHE01BL001-BL01&EFS.001 | =G01NHE01&MFB.001 |  |  | U012UNA01UH100
=G01NHE01BL001 | G01NHE01BL001-BL02 | =G01NHE01BL001-BL02;XQ01 | ELY1 O2 TRT LVL MEAS LVL2 ANALOG1 | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM LEVEL MEASUREMENT SYSTEM LEVEL MEASUREMENT SYSTEM 1 O2 WATER LEVEL MEASUREMENT ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BL | Level Measurement System | 001 | Level Measurement System 1 | -BL02 | O2 Water Level Measurement | XQ01 | Analog process signal | Ely1 | O2 TRT | Lvl Meas | Lvl2 | ANALOG1 | -BL02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | LIC | 0 mm | 1000 mm |  |  |  | ASHH |  | AH |  | AL |  | ASLL |  | No |  | =G01NHY01KF001+U012UNA01UH100-KF11 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 14 | =G01NHE01BL001-BL02&EFS.001 | =G01NHE01&MFB.001 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-BF02 | =G01NHC01BQ001-BF02;XG01 | ELY1 H2 TRT QUAL FLOW2 CB ON/OPN/MAX1 | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM 10301; FLOWMETER GENERAL CHECK BACK ON/OPEN // LIMIT VALUE >MAX 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -BF02 | 10301; Flowmeter general | XG01 | Check back on/open // Limit value >max 1 | Ely1 | H2 TRT | QUAL | Flow2 | CB ON/OPN/MAX1 | -BF02 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | FSZ | [7 empty] | AH |  | AL |  |  |  | Yes |  | =G01NHY01KF001+U012UNA01UH100-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XG01 | EA01 | 04 | =G01NHC01BQ001-BF02&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-BF10 | =G01NHC01BQ001-BF10;XG02 | ELY1 H2 TRT QUAL FLOW1 CB ON/OPN/MIN1 | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM 10301; FLOWMETER GENERAL CHECK BACK OFF/CLOSED // LIMIT VALUE >MIN 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -BF10 | 10301; Flowmeter general | XG02 | Check back off/closed // Limit value >min 1 | Ely1 | H2 TRT | QUAL | Flow1 | CB ON/OPN/MIN1 | -BF10 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | FS | [9 empty] | AL | [5 empty] | =G01NHY01KF001+U012UNA01UH100-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XG02 | EA01 | 05 | =G01NHC01BQ001-BF10&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01GT001 | G01NHE01GT001-BT01 | =G01NHE01GT001-BT01;XQ01 | ELY1 O2 TRT LEAD OFF TEMP1 ANALOG1 | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM GAS LEAD OFF SYSTEMS GAS LEAD OFF SYSTEM 1 TEMPERATURE MEASUREMENT - GAS COOLER O2 OUTLET ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | GT | Gas Lead off Systems | 001 | Gas Lead off System 1 | -BT01 | Temperature Measurement - Gas Cooler O2 outlet | XQ01 | Analog process signal | Ely1 | O2 TRT | Lead Off | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TIC | -20 °C | 100 °C | [13 empty] | =G01NHY01KF001+U012UNA01UH100-KF12 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 04 | =G01NHE01GT001-BT01&EFS.001 | =G01NHE01&MFB.002 |  |  | U012UNA01UH100
=G01NHE01GT001 | G01NHE01GT001-QN01 | =G01NHE01GT001-QN01;XQ01 | ELY1 O2 TRT LEAD OFF CV1 ANALOG1 | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM GAS LEAD OFF SYSTEMS GAS LEAD OFF SYSTEM 1 CONTROL VALVE - O2 BLOW OFF ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | GT | Gas Lead off Systems | 001 | Gas Lead off System 1 | -QN01 | Control valve - O2 Blow off | XQ01 | Analog process signal | Ely1 | O2 TRT | Lead Off | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF12 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 10 | =G01NHE01GT001-QN01&EFS.001 | =G01NHE01&MFB.002 |  |  | U012UNA01UH100
=G01NHE01HP001 | G01NHE01HP001-BP01 | =G01NHE01HP001-BP01;XQ01 | ELY1 O2 TRT SYS 1 PRES1 ANALOG1 | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM GAS COOLING SYSTEMS GAS COOLING SYSTEM 1 PRESSURE - O2 HEADER ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | HP | Gas Cooling Systems | 001 | Gas Cooling System 1 | -BP01 | Pressure - O2 Header | XQ01 | Analog process signal | Ely1 | O2 TRT | SYS 1 | Pres1 | ANALOG1 | -BP01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | PI | -25 mbar | 225 mbar | [7 empty] | AZL |  |  |  | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF07 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | B10:XQ01 | XQ01 | 02 | =G01NHE01HP001-BP01&EFS.001 | =G01NHE01&MFB.001 |  |  | U012UNA01UH100
=G01NHE01HP001 | G01NHE01HP001-BP02 | =G01NHE01HP001-BP02;XQ01 | ELY1 O2 TRT SYS 1 PRES2 ANALOG1 | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM GAS COOLING SYSTEMS GAS COOLING SYSTEM 1 PRESSURE - O2 HEADER ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | HP | Gas Cooling Systems | 001 | Gas Cooling System 1 | -BP02 | Pressure - O2 Header | XQ01 | Analog process signal | Ely1 | O2 TRT | SYS 1 | Pres2 | ANALOG1 | -BP02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | PIC | -25 mbar | 225 mbar |  |  |  | ASHH |  | AH | [7 empty] | =G01NHY01KF001+U012UNA01UH100-KF12 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 01 | =G01NHE01HP001-BP02&EFS.001 | =G01NHE01&MFB.001 |  |  | U012UNA01UH100
=G01NHE01HP001 | G01NHE01HP001-BT01 | =G01NHE01HP001-BT01;XQ01 | ELY1 O2 TRT SYS 1 TEMP1 ANALOG1 | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM GAS COOLING SYSTEMS GAS COOLING SYSTEM 1 TEMPERATURE GAS COOLER O2 INLET ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | HP | Gas Cooling Systems | 001 | Gas Cooling System 1 | -BT01 | Temperature Gas Cooler O2 Inlet | XQ01 | Analog process signal | Ely1 | O2 TRT | SYS 1 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | -20 °C | 100 °C | [13 empty] | =G01NHY01KF001+U012UNA01UH100-KF12 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 03 | =G01NHE01HP001-BT01&EFS.001 | =G01NHE01&MFB.002 |  |  | U012UNA01UH100
=G01NHG01QM001 | G01NHG01QM001-QN01 | =G01NHG01QM001-QN01;XQ01 | ELY1 PROC WTR SUP DIST CV1 ANALOG1 | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 WATER SUPPLY SYSTEMS PROCESS WATER SUPPLY SYSTEM PROCESS WATER DISTRIBUTION SYSTEMS PROCESS WATER DISTRIBUTION SYSTEM CONTROL VALVE - DEMIN WATER SUPPLY ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHG | Water Supply Systems | 01 | Process Water Supply System | QM | Process Water Distribution Systems | 001 | Process Water Distribution System | -QN01 | Control valve - Demin Water Supply | XQ01 | Analog process signal | Ely1 | Proc Wtr Sup | DIST | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF12 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 11 | =G01NHG01QM001-QN01&EFS.001 | =G01NHC01&MFB.001 |  |  | U012UNA01UH100
=G01NHH01HP001 | G01NHH01HP001-BF01 | =G01NHH01HP001-BF01;XQ01 | ELY1 PROC WTR REF SYS 1 FLOW1 ANALOG1 | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 PROCESS WATER REFINEMENT PROCESS WATER REFINEMENT LOOP PROCESS WATER REFINEMENT UNIT PROCESS WATER REFINEMENT UNIT 1 FLOWMETER - PUMP OUTPUT ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHH | Process Water Refinement | 01 | Process Water Refinement Loop | HP | Process Water Refinement Unit | 001 | Process Water Refinement Unit 1 | -BF01 | Flowmeter - Pump Output | XQ01 | Analog process signal | Ely1 | Proc Wtr Ref | SYS 1 | Flow1 | ANALOG1 | -BF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | FIC | 5 m³/h | 30 m³/h | [7 empty] | AL |  | ASLL |  |  |  | =G01NHY01KF001+U012UNA01UH100-KF11 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 01 | =G01NHH01HP001-BF01&EFS.001 | =G01NHH01&MFB.001 |  |  | U012UNA01UH100
=G01NHH01HP001 | G01NHH01HP001-BF20 | =G01NHH01HP001-BF20;XQ01 | ELY1 PROC WTR REF SYS 1 FLOW2 ANALOG1 | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 PROCESS WATER REFINEMENT PROCESS WATER REFINEMENT LOOP PROCESS WATER REFINEMENT UNIT PROCESS WATER REFINEMENT UNIT 1 FLOWMETER - OUTPUT H2 SIDE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHH | Process Water Refinement | 01 | Process Water Refinement Loop | HP | Process Water Refinement Unit | 001 | Process Water Refinement Unit 1 | -BF20 | Flowmeter - Output H2 side | XQ01 | Analog process signal | Ely1 | Proc Wtr Ref | SYS 1 | Flow2 | ANALOG1 | -BF20 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | FI | 5 m³/s | 30 m³/s | [13 empty] | =G01NHY01KF001+U012UNA01UH100-KF11 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 02 | =G01NHH01HP001-BF20&EFS.001 | =G01NHH01&MFB.001 |  |  | U012UNA01UH100
=G01NHH01HP001 | G01NHH01HP001-BF30 | =G01NHH01HP001-BF30;XQ01 | ELY1 PROC WTR REF SYS 1 FLOW3 ANALOG1 | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 PROCESS WATER REFINEMENT PROCESS WATER REFINEMENT LOOP PROCESS WATER REFINEMENT UNIT PROCESS WATER REFINEMENT UNIT 1 FLOWMETER - OUTPUT O2 SIDE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHH | Process Water Refinement | 01 | Process Water Refinement Loop | HP | Process Water Refinement Unit | 001 | Process Water Refinement Unit 1 | -BF30 | Flowmeter - Output O2 side | XQ01 | Analog process signal | Ely1 | Proc Wtr Ref | SYS 1 | Flow3 | ANALOG1 | -BF30 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | FIC | 5 m³/s | 30 m³/s | [5 empty] | AH |  | AL | [5 empty] | =G01NHY01KF001+U012UNA01UH100-KF11 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 03 | =G01NHH01HP001-BF30&EFS.001 | =G01NHH01&MFB.001 |  |  | U012UNA01UH100
=G01NHH01HP001 | G01NHH01HP001-BP02 | =G01NHH01HP001-BP02;XQ01 | ELY1 PROC WTR REF SYS 1 PRES2 ANALOG1 | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 PROCESS WATER REFINEMENT PROCESS WATER REFINEMENT LOOP PROCESS WATER REFINEMENT UNIT PROCESS WATER REFINEMENT UNIT 1 PRESSURE TRANSMITTER - PUMP OUTLET ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHH | Process Water Refinement | 01 | Process Water Refinement Loop | HP | Process Water Refinement Unit | 001 | Process Water Refinement Unit 1 | -BP02 | Pressure Transmitter - Pump Outlet | XQ01 | Analog process signal | Ely1 | Proc Wtr Ref | SYS 1 | Pres2 | ANALOG1 | -BP02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | PI | 0 bar | 6 bar | [13 empty] | =G01NHY01KF001+U012UNA01UH100-KF11 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 04 | =G01NHH01HP001-BP02&EFS.001 | =G01NHH01&MFB.001 |  |  | U012UNA01UH100
=G01NHH01HP001 | G01NHH01HP001-BQ01 | =G01NHH01HP001-BQ01;XQ02 | ELY1 PROC WTR REF SYS 1 QUAL1 ANALOG2 | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 PROCESS WATER REFINEMENT PROCESS WATER REFINEMENT LOOP PROCESS WATER REFINEMENT UNIT PROCESS WATER REFINEMENT UNIT 1 CONDUCTIVITY - WATER REFINEMENT INLET ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHH | Process Water Refinement | 01 | Process Water Refinement Loop | HP | Process Water Refinement Unit | 001 | Process Water Refinement Unit 1 | -BQ01 | Conductivity - Water Refinement Inlet | XQ02 | Analog process signal | Ely1 | Proc Wtr Ref | SYS 1 | Qual1 | ANALOG2 | -BQ01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | 0 µS/cm | 20 µS/cm | [13 empty] | =G01NHY01KF001+U012UNA01UH100-KF11 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | XD44:3M | 2e | 06 | =G01NHH01HP001-BQ01&EFS.001 | =G01NHH01&MFB.001 |  |  | U012UNA01UH100
=G01NHH01HP001 | G01NHH01HP001-BQ01 | =G01NHH01HP001-BQ01;XQ01 | ELY1 PROC WTR REF SYS 1 QUAL1 ANALOG1 | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 PROCESS WATER REFINEMENT PROCESS WATER REFINEMENT LOOP PROCESS WATER REFINEMENT UNIT PROCESS WATER REFINEMENT UNIT 1 CONDUCTIVITY - WATER REFINEMENT INLET ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHH | Process Water Refinement | 01 | Process Water Refinement Loop | HP | Process Water Refinement Unit | 001 | Process Water Refinement Unit 1 | -BQ01 | Conductivity - Water Refinement Inlet | XQ01 | Analog process signal | Ely1 | Proc Wtr Ref | SYS 1 | Qual1 | ANALOG1 | -BQ01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | AI | 0 µS/cm | 20 µS/cm |  |  |  | AHH |  | AH | [7 empty] | =G01NHY01KF001+U012UNA01UH100-KF11 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | XD44:3M | 1b | 05 | =G01NHH01HP001-BQ01&EFS.001 | =G01NHH01&MFB.001 |  |  | U012UNA01UH100
=G01NHH01HP001 | G01NHH01HP001-BQ02 | =G01NHH01HP001-BQ02;XQ02 | ELY1 PROC WTR REF SYS 1 QUAL2 ANALOG2 | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 PROCESS WATER REFINEMENT PROCESS WATER REFINEMENT LOOP PROCESS WATER REFINEMENT UNIT PROCESS WATER REFINEMENT UNIT 1 CONDUCTIVITY - WATER REFINEMENT OUTLET ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHH | Process Water Refinement | 01 | Process Water Refinement Loop | HP | Process Water Refinement Unit | 001 | Process Water Refinement Unit 1 | -BQ02 | Conductivity - Water Refinement Outlet | XQ02 | Analog process signal | Ely1 | Proc Wtr Ref | SYS 1 | Qual2 | ANALOG2 | -BQ02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | 0 µS/cm | 20 µS/cm | [13 empty] | =G01NHY01KF001+U012UNA01UH100-KF11 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | XD44:3M | 3f | 08 | =G01NHH01HP001-BQ02&EFS.001 | =G01NHH01&MFB.001 |  |  | U012UNA01UH100
=G01NHH01HP001 | G01NHH01HP001-BQ02 | =G01NHH01HP001-BQ02;XQ01 | ELY1 PROC WTR REF SYS 1 QUAL2 ANALOG1 | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 PROCESS WATER REFINEMENT PROCESS WATER REFINEMENT LOOP PROCESS WATER REFINEMENT UNIT PROCESS WATER REFINEMENT UNIT 1 CONDUCTIVITY - WATER REFINEMENT OUTLET ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHH | Process Water Refinement | 01 | Process Water Refinement Loop | HP | Process Water Refinement Unit | 001 | Process Water Refinement Unit 1 | -BQ02 | Conductivity - Water Refinement Outlet | XQ01 | Analog process signal | Ely1 | Proc Wtr Ref | SYS 1 | Qual2 | ANALOG1 | -BQ02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | AI | 0 µS/cm | 20 µS/cm |  |  |  | AHH |  | AH | [7 empty] | =G01NHY01KF001+U012UNA01UH100-KF11 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | XD44:3M | 3g | 07 | =G01NHH01HP001-BQ02&EFS.001 | =G01NHH01&MFB.001 |  |  | U012UNA01UH100
=G01NHH01HP001 | G01NHH01HP001-BQ03 | =G01NHH01HP001-BQ03;XQ02 | ELY1 PROC WTR REF SYS 1 QUAL3 ANALOG2 | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 PROCESS WATER REFINEMENT PROCESS WATER REFINEMENT LOOP PROCESS WATER REFINEMENT UNIT PROCESS WATER REFINEMENT UNIT 1 CONDUCTIVITY - WATER REFINEMENT OUTLET ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHH | Process Water Refinement | 01 | Process Water Refinement Loop | HP | Process Water Refinement Unit | 001 | Process Water Refinement Unit 1 | -BQ03 | Conductivity - Water Refinement Outlet | XQ02 | Analog process signal | Ely1 | Proc Wtr Ref | SYS 1 | Qual3 | ANALOG2 | -BQ03 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | 0 µS/cm | 20 µS/cm | [13 empty] | =G01NHY01KF001+U012UNA01UH100-KF11 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ02 | XQ02B | 10 | =G01NHH01HP001-BQ03&EFS.001 | =G01NHH01&MFB.001 |  |  | U012UNA01UH100
=G01NHH01HP001 | G01NHH01HP001-BQ03 | =G01NHH01HP001-BQ03;XQ01 | ELY1 PROC WTR REF SYS 1 QUAL3 ANALOG1 | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 PROCESS WATER REFINEMENT PROCESS WATER REFINEMENT LOOP PROCESS WATER REFINEMENT UNIT PROCESS WATER REFINEMENT UNIT 1 CONDUCTIVITY - WATER REFINEMENT OUTLET ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHH | Process Water Refinement | 01 | Process Water Refinement Loop | HP | Process Water Refinement Unit | 001 | Process Water Refinement Unit 1 | -BQ03 | Conductivity - Water Refinement Outlet | XQ01 | Analog process signal | Ely1 | Proc Wtr Ref | SYS 1 | Qual3 | ANALOG1 | -BQ03 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | AI | 0 µS/cm | 20 µS/cm | [13 empty] | =G01NHY01KF001+U012UNA01UH100-KF11 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | XD44:3M | 4h | 09 | =G01NHH01HP001-BQ03&EFS.001 | =G01NHH01&MFB.001 |  |  | U012UNA01UH100
=G01NHH01HP001 | G01NHH01HP001-QN01 | =G01NHH01HP001-QN01;XQ01 | ELY1 PROC WTR REF SYS 1 CV1 ANALOG1 | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 PROCESS WATER REFINEMENT PROCESS WATER REFINEMENT LOOP PROCESS WATER REFINEMENT UNIT PROCESS WATER REFINEMENT UNIT 1 3-WAY CONTROL VALVE - WATER REFINEMENT SKID ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHH | Process Water Refinement | 01 | Process Water Refinement Loop | HP | Process Water Refinement Unit | 001 | Process Water Refinement Unit 1 | -QN01 | 3-way control valve - Water Refinement Skid | XQ01 | Analog process signal | Ely1 | Proc Wtr Ref | SYS 1 | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF11 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 11 | =G01NHH01HP001-QN01&EFS.001 | =G01NHH01&MFB.001 |  |  | U012UNA01UH100
=G01NHP01WP001 | G01NHP01WP001-BT01 | =G01NHP01WP001-BT01;XQ01 | ELY1 HEAT DISS PIPING TEMP1 ANALOG1 | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 HEAT DISSIPATION SYSTEMS HEAT DISSIPATION (ELECTROLYSER SYSTEM) DISTRIBUTION COOLING WATER (ELECTROLYSER SYSTEM) PLANT COOLING WATER PIPE SYSTEM TEMPERATURE - WCR GAS COOLER H2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHP | Heat Dissipation Systems | 01 | Heat dissipation (Electrolyser System) | WP | Distribution Cooling Water (Electrolyser System) | 001 | Plant Cooling Water Pipe System | -BT01 | Temperature - WCR Gas Cooler H2 | XQ01 | Analog process signal | Ely1 | Heat Diss | Piping | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | -20 °C | 100 °C | [13 empty] | =G01NHY01KF001+U012UNA01UH100-KF12 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 06 | =G01NHP01WP001-BT01&EFS.001 | =G01NHC01&MFB.002 |  |  | U012UNA01UH100
=G01NHP01WP001 | G01NHP01WP001-BT02 | =G01NHP01WP001-BT02;XQ01 | ELY1 HEAT DISS PIPING TEMP2 ANALOG1 | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 HEAT DISSIPATION SYSTEMS HEAT DISSIPATION (ELECTROLYSER SYSTEM) DISTRIBUTION COOLING WATER (ELECTROLYSER SYSTEM) PLANT COOLING WATER PIPE SYSTEM TEMPERATURE - WCR GAS COOLER O2 ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHP | Heat Dissipation Systems | 01 | Heat dissipation (Electrolyser System) | WP | Distribution Cooling Water (Electrolyser System) | 001 | Plant Cooling Water Pipe System | -BT02 | Temperature - WCR Gas Cooler O2 | XQ01 | Analog process signal | Ely1 | Heat Diss | Piping | Temp2 | ANALOG1 | -BT02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | -20 °C | 100 °C | [13 empty] | =G01NHY01KF001+U012UNA01UH100-KF12 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 08 | =G01NHP01WP001-BT02&EFS.001 | =G01NHE01&MFB.002 |  |  | U012UNA01UH100
=G01NHP01WP001 | G01NHP01WP001-QN01 | =G01NHP01WP001-QN01;XQ01 | ELY1 HEAT DISS PIPING CV1 ANALOG1 | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 HEAT DISSIPATION SYSTEMS HEAT DISSIPATION (ELECTROLYSER SYSTEM) DISTRIBUTION COOLING WATER (ELECTROLYSER SYSTEM) PLANT COOLING WATER PIPE SYSTEM CONTROL VALVE - GAS COOLER H2 COOLING WATER ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHP | Heat Dissipation Systems | 01 | Heat dissipation (Electrolyser System) | WP | Distribution Cooling Water (Electrolyser System) | 001 | Plant Cooling Water Pipe System | -QN01 | Control Valve - Gas Cooler H2 Cooling Water | XQ01 | Analog process signal | Ely1 | Heat Diss | Piping | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF12 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 15 | =G01NHP01WP001-QN01&EFS.001 | =G01NHC01&MFB.002 |  |  | U012UNA01UH100
=G01NHP01WP001 | G01NHP01WP001-QN02 | =G01NHP01WP001-QN02;XQ01 | ELY1 HEAT DISS PIPING CV2 ANALOG1 | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 HEAT DISSIPATION SYSTEMS HEAT DISSIPATION (ELECTROLYSER SYSTEM) DISTRIBUTION COOLING WATER (ELECTROLYSER SYSTEM) PLANT COOLING WATER PIPE SYSTEM CONTROL VALVE - GAS COOLER O2 COOLING WATER ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHP | Heat Dissipation Systems | 01 | Heat dissipation (Electrolyser System) | WP | Distribution Cooling Water (Electrolyser System) | 001 | Plant Cooling Water Pipe System | -QN02 | Control Valve - Gas Cooler O2 Cooling Water | XQ01 | Analog process signal | Ely1 | Heat Diss | Piping | CV2 | ANALOG1 | -QN02KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF12 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 16 | =G01NHP01WP001-QN02&EFS.001 | =G01NHE01&MFB.002 |  |  | U012UNA01UH100
=G01NHX01QN001 | G01NHX01QN001-BF01 | =G01NHX01QN001-BF01;XQ01 | ELY1 N2 DIST CTRL H2 FLOW1 ANALOG1 | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION H2 FLOWMETER - NITROGEN H2 SIDE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 001 | Nitrogen Regulation H2 | -BF01 | Flowmeter - Nitrogen H2 side | XQ01 | Analog process signal | Ely1 | N2 Dist | CTRL H2 | Flow1 | ANALOG1 | -BF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | FI | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF11 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 13 | =G01NHX01QN001-BF01&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=G01NHX01QN001 | G01NHX01QN001-BP01 | =G01NHX01QN001-BP01;XQ01 | ELY1 N2 DIST CTRL H2 PRES1 ANALOG1 | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION H2 PRESSURE - NITROGEN H2 SIDE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 001 | Nitrogen Regulation H2 | -BP01 | Pressure - Nitrogen H2 side | XQ01 | Analog process signal | Ely1 | N2 Dist | CTRL H2 | Pres1 | ANALOG1 | -BP01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | PIZ | 0 bar | 2,5 bar | [5 empty] | AH |  | AL |  | ASLL |  | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF07 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | XG07:6 | 6d | 03 | =G01NHX01QN001-BP01&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=G01NHX01QN001 | G01NHX01QN001-BT01 | =G01NHX01QN001-BT01;XQ01 | ELY1 N2 DIST CTRL H2 TEMP1 ANALOG1 | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION H2 TEMPERATURE - NITROGEN INLET ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 001 | Nitrogen Regulation H2 | -BT01 | Temperature - Nitrogen Inlet | XQ01 | Analog process signal | Ely1 | N2 Dist | CTRL H2 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | -20 °C | 100 °C | [13 empty] | =G01NHY01KF001+U012UNA01UH100-KF12 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 02 | =G01NHX01QN001-BT01&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=G01NHX01QN001 | G01NHX01QN001-QN01 | =G01NHX01QN001-QN01;XQ01 | ELY1 N2 DIST CTRL H2 CV1 ANALOG1 | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION H2 CONTROL VALVE - NITROGEN H2 SIDE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 001 | Nitrogen Regulation H2 | -QN01 | Control valve - Nitrogen H2 side | XQ01 | Analog process signal | Ely1 | N2 Dist | CTRL H2 | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF12 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 12 | =G01NHX01QN001-QN01&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=G01NHX01QN002 | G01NHX01QN002-BF01 | =G01NHX01QN002-BF01;XQ01 | ELY1 N2 DIST CTRL O2 FLOW1 ANALOG1 | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION O2 FLOWMETER - NITROGEN O2 SIDE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 002 | Nitrogen Regulation O2 | -BF01 | Flowmeter - Nitrogen O2 side | XQ01 | Analog process signal | Ely1 | N2 Dist | CTRL O2 | Flow1 | ANALOG1 | -BF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | FI | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF11 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 12 | =G01NHX01QN002-BF01&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=G01NHX01QN002 | G01NHX01QN002-BP01 | =G01NHX01QN002-BP01;XQ01 | ELY1 N2 DIST CTRL O2 PRES1 ANALOG1 | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION O2 PRESSURE - NITROGEN O2 SIDE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 002 | Nitrogen Regulation O2 | -BP01 | Pressure - Nitrogen O2 side | XQ01 | Analog process signal | Ely1 | N2 Dist | CTRL O2 | Pres1 | ANALOG1 | -BP01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | PIZ | 0 bar | 2,5 bar | [5 empty] | AH |  | AL |  | ASLL |  | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF07 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | XG07:8 | 8d | 04 | =G01NHX01QN002-BP01&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=G01NHX01QN002 | G01NHX01QN002-QN01 | =G01NHX01QN002-QN01;XQ01 | ELY1 N2 DIST CTRL O2 CV1 ANALOG1 | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION O2 CONTROL VALVE - NITROGEN O2 SIDE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 002 | Nitrogen Regulation O2 | -QN01 | Control valve - Nitrogen O2 side | XQ01 | Analog process signal | Ely1 | N2 Dist | CTRL O2 | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF12 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XQ01 | EA01 | 14 | =G01NHX01QN002-QN01&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=V01NHC10WP002 | V01NHC10WP002-BP01 | =V01NHC10WP002-BP01;XQ01 | GAS TRT H2 LEAD OFF PIPING PRES1 ANALOG1 | 40 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT GAS LEAD OFF GAS LEAD OFF SYSTEMS PRODUCT GAS LINE 10922; GAUGE PRESSURE TRANSM. WITHOUT PRESSURE REPEATER ANALOG PROCESS SIGNAL | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 10 | Gas Lead off | WP | Gas Lead off Systems | 002 | Product Gas Line | -BP01 | 10922; Gauge pressure transm. without pressure repeater | XQ01 | Analog process signal | Gas TRT | H2 Lead Off | Piping | Pres1 | ANALOG1 | -BP01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | PI | [9 empty] | AL |  | ASLL | [9 empty] | =V01NHC20&MFB.001
=V01NHC20CM001 | V01NHC20CM001-BL01 | =V01NHC20CM001-BL01;XQ01 | GAS TRT H2 LP BUF TNK1 LVL1 ANALOG1 | 35 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 BUFFER TANK BUFFER TANK SYSTEMS BUFFER TANK SYSTEM 10751; RADIOACTIVE LEVEL METER, COMP. SYST. ANALOG PROCESS SIGNAL | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 20 | H2 Buffer Tank | CM | Buffer Tank Systems | 001 | Buffer Tank System | -BL01 | 10751; Radioactive level meter, comp. syst. | XQ01 | Analog process signal | Gas TRT | H2 LP Buf | Tnk1 | Lvl1 | ANALOG1 | -BL01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | LIZ | [5 empty] | AZHH | [5 empty] | AZLL |  | Yes | SIL 2 | [6 empty] | =V01NHC20&MFB.001
=V01NHC20CM001 | V01NHC20CM001-BL02 | =V01NHC20CM001-BL02;XQ01 | GAS TRT H2 LP BUF TNK1 LVL2 ANALOG1 | 35 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 BUFFER TANK BUFFER TANK SYSTEMS BUFFER TANK SYSTEM 10751; RADIOACTIVE LEVEL METER, COMP. SYST. ANALOG PROCESS SIGNAL | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 20 | H2 Buffer Tank | CM | Buffer Tank Systems | 001 | Buffer Tank System | -BL02 | 10751; Radioactive level meter, comp. syst. | XQ01 | Analog process signal | Gas TRT | H2 LP Buf | Tnk1 | Lvl2 | ANALOG1 | -BL02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | LI | [5 empty] | ASHH |  | AH |  | AL |  | ASLL | [9 empty] | =V01NHC20&MFB.001
=V01NHC20CM001 | V01NHC20CM001-BP01 | =V01NHC20CM001-BP01;XQ01 | GAS TRT H2 LP BUF TNK1 PRES1 ANALOG1 | 36 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 BUFFER TANK BUFFER TANK SYSTEMS BUFFER TANK SYSTEM 10922; GAUGE PRESSURE TRANSM. WITHOUT PRESSURE REPEATER ANALOG PROCESS SIGNAL | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 20 | H2 Buffer Tank | CM | Buffer Tank Systems | 001 | Buffer Tank System | -BP01 | 10922; Gauge pressure transm. without pressure repeater | XQ01 | Analog process signal | Gas TRT | H2 LP Buf | Tnk1 | Pres1 | ANALOG1 | -BP01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | PI | [9 empty] | AL |  | ASLL | [9 empty] | =V01NHC20&MFB.001
=V01NHC20CM001 | V01NHC20CM001-BT01 | =V01NHC20CM001-BT01;XQ01 | GAS TRT H2 LP BUF TNK1 TEMP1 ANALOG1 | 36 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 BUFFER TANK BUFFER TANK SYSTEMS BUFFER TANK SYSTEM 11332; RTD THERMOMETER WITHOUT CONDUIT ANALOG PROCESS SIGNAL | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 20 | H2 Buffer Tank | CM | Buffer Tank Systems | 001 | Buffer Tank System | -BT01 | 11332; RTD thermometer without conduit | XQ01 | Analog process signal | Gas TRT | H2 LP Buf | Tnk1 | Temp1 | ANALOG1 | -BT01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | [21 empty] | =V01NHC20&MFB.001
=V01NHC30WP001 | V01NHC30WP001-BP01 | =V01NHC30WP001-BP01;XQ01 | GAS TRT H2 COMPR PIPING PRES1 ANALOG1 | 37 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 30BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM INLET LINE GENERAL POSITION ANALOG PROCESS SIGNAL | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 30 | H2 Compressor System 30bar | WP | Compressor Pipe Systems | 001 | Compressor Pipe System Inlet Line | -BP01 | General Position | XQ01 | Analog process signal | Gas TRT | H2 Compr | Piping | Pres1 | ANALOG1 |  | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | PIC | [21 empty] | =V01NHC30&MFB.001
=V01NHC31WP001 | V01NHC31WP001-BP01 | =V01NHC31WP001-BP01;XQ01 | GAS TRT H2 COMPR PIPING PRES1 ANALOG1 | 37 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 100BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM INLET LINE GENERAL POSITION ANALOG PROCESS SIGNAL | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 31 | H2 Compressor System 100bar | WP | Compressor Pipe Systems | 001 | Compressor Pipe System Inlet Line | -BP01 | General Position | XQ01 | Analog process signal | Gas TRT | H2 Compr | Piping | Pres1 | ANALOG1 | DR | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | PIC | [21 empty] | =V01NHC31&MFB.001
=V01NHC60BZ001 | V01NHC60BZ001-BF01 | =V01NHC60BZ001-BF01;XQ01 | GAS TRT H2 HANDOVR MEAS1 FLOW1 ANALOG1 | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIC SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 10301; FLOWMETER GENERAL ANALOG PROCESS SIGNAL | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 60 | Product Gas Analytic System | BZ | Measurement Systems | 001 | Measurement System 1 | -BF01 | 10301; Flowmeter general | XQ01 | Analog process signal | Gas TRT | H2 Handovr | Meas1 | Flow1 | ANALOG1 | DR | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | FI | [21 empty] | =V01NHC60&MFB.001
=V01NHC60BZ001 | V01NHC60BZ001-BP01 | =V01NHC60BZ001-BP01;XQ01 | GAS TRT H2 HANDOVR MEAS1 PRES1 ANALOG1 | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIC SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 10922; GAUGE PRESSURE TRANSM. WITHOUT PRESSURE REPEATER ANALOG PROCESS SIGNAL | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 60 | Product Gas Analytic System | BZ | Measurement Systems | 001 | Measurement System 1 | -BP01 | 10922; Gauge pressure transm. without pressure repeater | XQ01 | Analog process signal | Gas TRT | H2 Handovr | Meas1 | Pres1 | ANALOG1 | DR | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | PI | [21 empty] | =V01NHC60&MFB.001
=V01NHC60BZ001 | V01NHC60BZ001-BT01 | =V01NHC60BZ001-BT01;XQ01 | GAS TRT H2 HANDOVR MEAS1 TEMP1 ANALOG1 | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIC SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 11332; RTD THERMOMETER WITHOUT CONDUIT ANALOG PROCESS SIGNAL | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 60 | Product Gas Analytic System | BZ | Measurement Systems | 001 | Measurement System 1 | -BT01 | 11332; RTD thermometer without conduit | XQ01 | Analog process signal | Gas TRT | H2 Handovr | Meas1 | Temp1 | ANALOG1 | DR | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | [21 empty] | =V01NHC60&MFB.001
=V01NHC61BZ001 | V01NHC61BZ001-BF01 | =V01NHC61BZ001-BF01;XQ01 | GAS TRT H2 HANDOVR MEAS1 FLOW1 ANALOG1 | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIK SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 10301; FLOWMETER GENERAL ANALOG PROCESS SIGNAL | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 61 | Product Gas Analytik System | BZ | Measurement Systems | 001 | Measurement System 1 | -BF01 | 10301; Flowmeter general | XQ01 | Analog process signal | Gas TRT | H2 Handovr | Meas1 | Flow1 | ANALOG1 | DR | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | FI | [21 empty] | =V01NHC61&MFB.001
=V01NHC61BZ001 | V01NHC61BZ001-BP01 | =V01NHC61BZ001-BP01;XQ01 | GAS TRT H2 HANDOVR MEAS1 PRES1 ANALOG1 | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIK SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 10922; GAUGE PRESSURE TRANSM. WITHOUT PRESSURE REPEATER ANALOG PROCESS SIGNAL | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 61 | Product Gas Analytik System | BZ | Measurement Systems | 001 | Measurement System 1 | -BP01 | 10922; Gauge pressure transm. without pressure repeater | XQ01 | Analog process signal | Gas TRT | H2 Handovr | Meas1 | Pres1 | ANALOG1 | DR | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | PI | [21 empty] | =V01NHC61&MFB.001
=V01NHC61BZ001 | V01NHC61BZ001-BT01 | =V01NHC61BZ001-BT01;XQ01 | GAS TRT H2 HANDOVR MEAS1 TEMP1 ANALOG1 | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIK SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 11332; RTD THERMOMETER WITHOUT CONDUIT ANALOG PROCESS SIGNAL | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 61 | Product Gas Analytik System | BZ | Measurement Systems | 001 | Measurement System 1 | -BT01 | 11332; RTD thermometer without conduit | XQ01 | Analog process signal | Gas TRT | H2 Handovr | Meas1 | Temp1 | ANALOG1 | DR | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 0 | TI | [21 empty] | =V01NHC61&MFB.001
=A01PAD01EZ001 | A01PAD01EZ001-EQ01GQ01 | PAD01EZ001-EQ01GQ01;YQ01 | AUX COOL WTR RECOOL AIR1-1 ANALOG1 | 34 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING SYSTEMS RECOOLING CIRCUIT AIR COOLED HEAT EXCHANGER 1 - 1 ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | EZ | Recooling Systems | 001 | Recooling Circuit | -EQ01GQ01 | Air Cooled Heat Exchanger 1 - 1 | YQ01 | Analog process signal | Aux | Cool Wtr | ReCool | Air1-1 | ANALOG1 |  | Electrical | Undefined | Undefined | Field bus | Undefined |  |  | AO | 0 | NS | [21 empty] | =A01PAD01&MFB.001
=A01PAD01EZ001 | A01PAD01EZ001-EQ01GQxx | PAD01EZ001-EQ01GQxx;YQ01 | AUX COOL WTR RECOOL AIR1-X ANALOG1 | 34 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING SYSTEMS RECOOLING CIRCUIT AIR COOLED HEAT EXCHANGER 1 - X ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | EZ | Recooling Systems | 001 | Recooling Circuit | -EQ01GQxx | Air Cooled Heat Exchanger 1 - x | YQ01 | Analog process signal | Aux | Cool Wtr | ReCool | Air1-x | ANALOG1 |  | Electrical | Undefined | Undefined | Field bus | Undefined |  |  | AO | 0 | NS | [21 empty] | =A01PAD01&MFB.001
=A01PAD01EZ001 | A01PAD01EZ001-EQ02GQ01 | PAD01EZ001-EQ02GQ01;YQ01 | AUX COOL WTR RECOOL AIR2-1 ANALOG1 | 34 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING SYSTEMS RECOOLING CIRCUIT AIR COOLED HEAT EXCHANGER 2 - 1 ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | EZ | Recooling Systems | 001 | Recooling Circuit | -EQ02GQ01 | Air Cooled Heat Exchanger 2 - 1 | YQ01 | Analog process signal | Aux | Cool Wtr | ReCool | Air2-1 | ANALOG1 |  | Electrical | Undefined | Undefined | Field bus | Undefined |  |  | AO | 0 | NS | [21 empty] | =A01PAD01&MFB.001
=A01PAD01EZ001 | A01PAD01EZ001-EQ02GQxx | PAD01EZ001-EQ02GQxx;YQ01 | AUX COOL WTR RECOOL AIR2-X ANALOG1 | 34 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING SYSTEMS RECOOLING CIRCUIT AIR COOLED HEAT EXCHANGER 2 - X ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | EZ | Recooling Systems | 001 | Recooling Circuit | -EQ02GQxx | Air Cooled Heat Exchanger 2 - x | YQ01 | Analog process signal | Aux | Cool Wtr | ReCool | Air2-x | ANALOG1 |  | Electrical | Undefined | Undefined | Field bus | Undefined |  |  | AO | 0 | NS | [21 empty] | =A01PAD01&MFB.001
=A01PAD01EZ001 | A01PAD01EZ001-EQ03GQ01 | PAD01EZ001-EQ03GQ01;YQ01 | AUX COOL WTR RECOOL AIR3-1 ANALOG1 | 34 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING SYSTEMS RECOOLING CIRCUIT AIR COOLED HEAT EXCHANGER 3 - 1 ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | EZ | Recooling Systems | 001 | Recooling Circuit | -EQ03GQ01 | Air Cooled Heat Exchanger 3 - 1 | YQ01 | Analog process signal | Aux | Cool Wtr | ReCool | Air3-1 | ANALOG1 |  | Electrical | Undefined | Undefined | Field bus | Undefined |  |  | AO | 0 | NS | [21 empty] | =A01PAD01&MFB.001
=A01PAD01EZ001 | A01PAD01EZ001-EQ03GQxx | PAD01EZ001-EQ03GQxx;YQ01 | AUX COOL WTR RECOOL AIR3-X ANALOG1 | 34 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING SYSTEMS RECOOLING CIRCUIT AIR COOLED HEAT EXCHANGER 3 - X ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | EZ | Recooling Systems | 001 | Recooling Circuit | -EQ03GQxx | Air Cooled Heat Exchanger 3 - x | YQ01 | Analog process signal | Aux | Cool Wtr | ReCool | Air3-x | ANALOG1 |  | Electrical | Undefined | Undefined | Field bus | Undefined |  |  | AO | 0 | NS | [21 empty] | =A01PAD01&MFB.001
=A01PAD01WP001 | A01PAD01WP001-QN01 | =A01PAD01WP001-QN01;YQ01 | AUX COOL WTR PIPING CV1 ANALOG1 | 31 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING WATER DISTRIBUTION SYSTEM COOLING WATER PIPE SYSTEM CONTROL VALVE - COMPRESSOR COOLINGWATER RETURN ANALOG PROCESS SIGNAL | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | WP | Recooling Water Distribution System | 001 | Cooling Water Pipe System | -QN01 | Control valve - Compressor Coolingwater Return | YQ01 | Analog process signal | Aux | Cool Wtr | Piping | CV1 | ANALOG1 | DR | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AO | 0 | YC | [17 empty] | B10:YQ01 | EA01 |  |  | =A01PAD01&MFB.002
=G01NHB01EQ001 | G01NHB01EQ001-QN01 | =G01NHB01EQ001-QN01;YQ01 | ELY1 GRP1 COOL CV1 ANALOG1 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 COOLING WATER - CONTROL VALVE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -QN01 | Cooling Water - Control Valve | YQ01 | Analog process signal | Ely1 | Grp1 | Cool | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AO | 0 | YC | [15 empty] | =G01NHB01KF002+U012UNA01UH111-KF01 | 6DL1 135-6TF00-0EH1, ET 200SP HA, AQ 8XI HART |  |  | 01 | =G01NHB01EQ001-QN01&EFS.001 | =G01NHB01&MFB.001 |  |  | U012UNA01UH111
=G01NHB02EQ001 | G01NHB02EQ001-QN01 | =G01NHB02EQ001-QN01;YQ01 | ELY1 GRP2 COOL CV1 ANALOG1 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 COOLING WATER - CONTROL VALVE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -QN01 | Cooling Water - Control Valve | YQ01 | Analog process signal | Ely1 | Grp2 | Cool | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AO | 0 | YC | [15 empty] | =G01NHB02KF002+U012UNA01UH121-KF01 | 6DL1 135-6TF00-0EH1, ET 200SP HA, AQ 8XI HART | B10:YQ01 | EA01 | 01 | =G01NHB02EQ001-QN01&EFS.001 | =G01NHB02&MFB.001 |  |  | U012UNA01UH121
=G01NHB03EQ001 | G01NHB03EQ001-QN01 | =G01NHB03EQ001-QN01;YQ01 | ELY1 GRP3 COOL CV1 ANALOG1 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 COOLING WATER - CONTROL VALVE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -QN01 | Cooling Water - Control Valve | YQ01 | Analog process signal | Ely1 | Grp3 | Cool | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AO | 0 | YC | [15 empty] | =G01NHB03KF002+U012UNA01UH131-KF01 | 6DL1 135-6TF00-0EH1, ET 200SP HA, AQ 8XI HART | B10:YQ01 | EA01 | 01 | =G01NHB03EQ001-QN01&EFS.001 | =G01NHB03&MFB.001 |  |  | U012UNA01UH131
=G01NHB04EQ001 | G01NHB04EQ001-QN01 | =G01NHB04EQ001-QN01;YQ01 | ELY1 GRP4 COOL CV1 ANALOG1 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 COOLING WATER - CONTROL VALVE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -QN01 | Cooling Water - Control Valve | YQ01 | Analog process signal | Ely1 | Grp4 | Cool | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AO | 0 | YC | [15 empty] | =G01NHB04KF002+U012UNA01UH141-KF01 | 6DL1 135-6TF00-0EH1, ET 200SP HA, AQ 8XI HART | B10:YQ01 | EA01 | 01 | =G01NHB04EQ001-QN01&EFS.001 | =G01NHB04&MFB.001 |  |  | U012UNA01UH141
=G01NHB05EQ001 | G01NHB05EQ001-QN01 | =G01NHB05EQ001-QN01;YQ01 | ELY1 GRP5 COOL CV1 ANALOG1 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 COOLING WATER - CONTROL VALVE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -QN01 | Cooling Water - Control Valve | YQ01 | Analog process signal | Ely1 | Grp5 | Cool | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AO | 0 | YC | [15 empty] | =G01NHB05KF002+U012UNA01UH151-KF01 | 6DL1 135-6TF00-0EH1, ET 200SP HA, AQ 8XI HART | B10:YQ01 | EA01 | 01 | =G01NHB05EQ001-QN01&EFS.001 | =G01NHB05&MFB.001 |  |  | U012UNA01UH151
=G01NHB06EQ001 | G01NHB06EQ001-QN01 | =G01NHB06EQ001-QN01;YQ01 | ELY1 GRP6 COOL CV1 ANALOG1 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 COOLING WATER - CONTROL VALVE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -QN01 | Cooling Water - Control Valve | YQ01 | Analog process signal | Ely1 | Grp6 | Cool | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AO | 0 | YC | [15 empty] | =G01NHB06KF002+U012UNA01UH161-KF01 | 6DL1 135-6TF00-0EH1, ET 200SP HA, AQ 8XI HART | B10:YQ01 | EA01 | 01 | =G01NHB06EQ001-QN01&EFS.001 | =G01NHB06&MFB.001 |  |  | U012UNA01UH161
=G01NHC01GT001 | G01NHC01GT001-QN01 | =G01NHC01GT001-QN01;YQ01 | ELY1 H2 TRT LEAD OFF CV1 ANALOG1 | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM GAS LEAD OFF SYSTEMS GAS LEAD OFF SYSTEM 1 CONTROL VALVE - H2 PRODUCT ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | GT | Gas Lead off Systems | 001 | Gas Lead off System 1 | -QN01 | Control valve - H2 Product | YQ01 | Analog process signal | Ely1 | H2 TRT | Lead Off | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AO | 0 | YC | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF14 | 6DL1 135-6TF00-0EH1, ET 200SP HA, AQ 8XI HART | B10:YQ01 | EA01 | 01 | =G01NHC01GT001-QN01&EFS.001 | =G01NHC01&MFB.002 |  |  | U012UNA01UH100
=G01NHC01GT001 | G01NHC01GT001-QN02 | =G01NHC01GT001-QN02;YQ01 | ELY1 H2 TRT LEAD OFF CV2 ANALOG1 | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM GAS LEAD OFF SYSTEMS GAS LEAD OFF SYSTEM 1 CONTROL VALVE - H2 BLOW OFF ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | GT | Gas Lead off Systems | 001 | Gas Lead off System 1 | -QN02 | Control valve - H2 Blow off | YQ01 | Analog process signal | Ely1 | H2 TRT | Lead Off | CV2 | ANALOG1 | -QN02KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AO | 0 | YC | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF14 | 6DL1 135-6TF00-0EH1, ET 200SP HA, AQ 8XI HART | B10:YQ01 | EA01 | 02 | =G01NHC01GT001-QN02&EFS.001 | =G01NHC01&MFB.002 |  |  | U012UNA01UH100
=G01NHE01GT001 | G01NHE01GT001-QN01 | =G01NHE01GT001-QN01;YQ01 | ELY1 O2 TRT LEAD OFF CV1 ANALOG1 | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM GAS LEAD OFF SYSTEMS GAS LEAD OFF SYSTEM 1 CONTROL VALVE - O2 BLOW OFF ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | GT | Gas Lead off Systems | 001 | Gas Lead off System 1 | -QN01 | Control valve - O2 Blow off | YQ01 | Analog process signal | Ely1 | O2 TRT | Lead Off | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AO | 0 | YC | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF14 | 6DL1 135-6TF00-0EH1, ET 200SP HA, AQ 8XI HART | B10:YQ01 | EA01 | 03 | =G01NHE01GT001-QN01&EFS.001 | =G01NHE01&MFB.002 |  |  | U012UNA01UH100
=G01NHG01QM001 | G01NHG01QM001-QN01 | =G01NHG01QM001-QN01;YQ01 | ELY1 PROC WTR SUP DIST CV1 ANALOG1 | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 WATER SUPPLY SYSTEMS PROCESS WATER SUPPLY SYSTEM PROCESS WATER DISTRIBUTION SYSTEMS PROCESS WATER DISTRIBUTION SYSTEM CONTROL VALVE - DEMIN WATER SUPPLY ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHG | Water Supply Systems | 01 | Process Water Supply System | QM | Process Water Distribution Systems | 001 | Process Water Distribution System | -QN01 | Control valve - Demin Water Supply | YQ01 | Analog process signal | Ely1 | Proc Wtr Sup | DIST | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AO | 0 | YC | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF14 | 6DL1 135-6TF00-0EH1, ET 200SP HA, AQ 8XI HART | B10:YQ01 | EA01 | 04 | =G01NHG01QM001-QN01&EFS.001 | =G01NHC01&MFB.001 |  |  | U012UNA01UH100
=G01NHH01HP001 | G01NHH01HP001-QN01 | =G01NHH01HP001-QN01;YQ01 | ELY1 PROC WTR REF SYS 1 CV1 ANALOG1 | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 PROCESS WATER REFINEMENT PROCESS WATER REFINEMENT LOOP PROCESS WATER REFINEMENT UNIT PROCESS WATER REFINEMENT UNIT 1 3-WAY CONTROL VALVE - WATER REFINEMENT SKID ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHH | Process Water Refinement | 01 | Process Water Refinement Loop | HP | Process Water Refinement Unit | 001 | Process Water Refinement Unit 1 | -QN01 | 3-way control valve - Water Refinement Skid | YQ01 | Analog process signal | Ely1 | Proc Wtr Ref | SYS 1 | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AO | 0 | YC | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF14 | 6DL1 135-6TF00-0EH1, ET 200SP HA, AQ 8XI HART | B10:YQ01 | EA01 | 05 | =G01NHH01HP001-QN01&EFS.001 | =G01NHH01&MFB.001 |  |  | U012UNA01UH100
=G01NHP01WP001 | G01NHP01WP001-QN01 | =G01NHP01WP001-QN01;YQ01 | ELY1 HEAT DISS PIPING CV1 ANALOG1 | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 HEAT DISSIPATION SYSTEMS HEAT DISSIPATION (ELECTROLYSER SYSTEM) DISTRIBUTION COOLING WATER (ELECTROLYSER SYSTEM) PLANT COOLING WATER PIPE SYSTEM CONTROL VALVE - GAS COOLER H2 COOLING WATER ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHP | Heat Dissipation Systems | 01 | Heat dissipation (Electrolyser System) | WP | Distribution Cooling Water (Electrolyser System) | 001 | Plant Cooling Water Pipe System | -QN01 | Control Valve - Gas Cooler H2 Cooling Water | YQ01 | Analog process signal | Ely1 | Heat Diss | Piping | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AO | 0 | YC | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF14 | 6DL1 135-6TF00-0EH1, ET 200SP HA, AQ 8XI HART | B10:YQ01 | EA01 | 06 | =G01NHP01WP001-QN01&EFS.001 | =G01NHC01&MFB.002 |  |  | U012UNA01UH100
=G01NHP01WP001 | G01NHP01WP001-QN02 | =G01NHP01WP001-QN02;YQ01 | ELY1 HEAT DISS PIPING CV2 ANALOG1 | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 HEAT DISSIPATION SYSTEMS HEAT DISSIPATION (ELECTROLYSER SYSTEM) DISTRIBUTION COOLING WATER (ELECTROLYSER SYSTEM) PLANT COOLING WATER PIPE SYSTEM CONTROL VALVE - GAS COOLER O2 COOLING WATER ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHP | Heat Dissipation Systems | 01 | Heat dissipation (Electrolyser System) | WP | Distribution Cooling Water (Electrolyser System) | 001 | Plant Cooling Water Pipe System | -QN02 | Control Valve - Gas Cooler O2 Cooling Water | YQ01 | Analog process signal | Ely1 | Heat Diss | Piping | CV2 | ANALOG1 | -QN02KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AO | 0 | YC | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF14 | 6DL1 135-6TF00-0EH1, ET 200SP HA, AQ 8XI HART | B10:YQ01 | EA01 | 07 | =G01NHP01WP001-QN02&EFS.001 | =G01NHE01&MFB.002 |  |  | U012UNA01UH100
=G01NHX01QN001 | G01NHX01QN001-QN01 | =G01NHX01QN001-QN01;YQ01 | ELY1 N2 DIST CTRL H2 CV1 ANALOG1 | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION H2 CONTROL VALVE - NITROGEN H2 SIDE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 001 | Nitrogen Regulation H2 | -QN01 | Control valve - Nitrogen H2 side | YQ01 | Analog process signal | Ely1 | N2 Dist | CTRL H2 | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AO | 0 | YC | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF14 | 6DL1 135-6TF00-0EH1, ET 200SP HA, AQ 8XI HART | B10:YQ01 | EA01 | 08 | =G01NHX01QN001-QN01&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=G01NHX01QN002 | G01NHX01QN002-QN01 | =G01NHX01QN002-QN01;YQ01 | ELY1 N2 DIST CTRL O2 CV1 ANALOG1 | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION O2 CONTROL VALVE - NITROGEN O2 SIDE ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 002 | Nitrogen Regulation O2 | -QN01 | Control valve - Nitrogen O2 side | YQ01 | Analog process signal | Ely1 | N2 Dist | CTRL O2 | CV1 | ANALOG1 | -QN01KF01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AO | 0 | YC | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF15 | 6DL1 135-6TF00-0EH1, ET 200SP HA, AQ 8XI HART | B10:YQ01 | EA01 | 01 | =G01NHX01QN002-QN01&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=A01PAD01WP001 | A01PAD01WP001-QN01 | =A01PAD01WP001-QN01;XU01 | AUX COOL WTR PIPING CV1 GRP FLT | 31 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING WATER DISTRIBUTION SYSTEM COOLING WATER PIPE SYSTEM CONTROL VALVE - COMPRESSOR COOLINGWATER RETURN GROUP FAULT ALARM | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | WP | Recooling Water Distribution System | 001 | Cooling Water Pipe System | -QN01 | Control valve - Compressor Coolingwater Return | XU01 | Group fault alarm | Aux | Cool Wtr | Piping | CV1 | GRP FLT | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | YC | [17 empty] | B10:XU01 | EA01 |  |  | =A01PAD01&MFB.002
=A01QJB01WP003 | A01QJB01WP003-QM11 | =A01QJB01WP003-QM11;XB01 | AUX N2 SUP PIPING SV11 CB ON/OPN | 32 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS NITROGEN SUPPLY SYSTEMS NITROGEN SUPPLY SYSTEM 1 PIPE SYSTEM NITROGEN SUPPLY AUX1 BALL VALVE (GENERAL) CHECK BACK ON/OPEN | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | QJB | Nitrogen Supply Systems | 01 | Nitrogen Supply System 1 | WP | Pipe System | 003 | Nitrogen Supply AUX1 | -QM11 | Ball valve (general) | XB01 | Check back on/open | Aux | N2 Sup | Piping | SV11 | CB ON/OPN | DR | Electrical | 24 VAC | 24 VAC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC10&MFB.001
=A01QJB01WP003 | A01QJB01WP003-QM11 | =A01QJB01WP003-QM11;XB02 | AUX N2 SUP PIPING SV11 CB OFF/CLD | 33 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS NITROGEN SUPPLY SYSTEMS NITROGEN SUPPLY SYSTEM 1 PIPE SYSTEM NITROGEN SUPPLY AUX1 BALL VALVE (GENERAL) CHECK BACK OFF/CLOSED | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | QJB | Nitrogen Supply Systems | 01 | Nitrogen Supply System 1 | WP | Pipe System | 003 | Nitrogen Supply AUX1 | -QM11 | Ball valve (general) | XB02 | Check back off/closed | Aux | N2 Sup | Piping | SV11 | CB OFF/CLD | DR | Electrical | 24 VAC | 24 VAC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC10&MFB.001
=A01QJB01WP003 | A01QJB01WP003-QM60 | =A01QJB01WP003-QM60;XB01 | AUX N2 SUP PIPING SV60 CB ON/OPN | 32 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS NITROGEN SUPPLY SYSTEMS NITROGEN SUPPLY SYSTEM 1 PIPE SYSTEM NITROGEN SUPPLY AUX1 BALL VALVE (GENERAL) CHECK BACK ON/OPEN | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | QJB | Nitrogen Supply Systems | 01 | Nitrogen Supply System 1 | WP | Pipe System | 003 | Nitrogen Supply AUX1 | -QM60 | Ball valve (general) | XB01 | Check back on/open | Aux | N2 Sup | Piping | SV60 | CB ON/OPN | -QM60BG01 | Electrical | 24 VAC | 24 VAC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =A01QJB01&MFB.001
=A01QJB01WP003 | A01QJB01WP003-QM60 | =A01QJB01WP003-QM60;XB02 | AUX N2 SUP PIPING SV60 CB OFF/CLD | 33 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS NITROGEN SUPPLY SYSTEMS NITROGEN SUPPLY SYSTEM 1 PIPE SYSTEM NITROGEN SUPPLY AUX1 BALL VALVE (GENERAL) CHECK BACK OFF/CLOSED | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | QJB | Nitrogen Supply Systems | 01 | Nitrogen Supply System 1 | WP | Pipe System | 003 | Nitrogen Supply AUX1 | -QM60 | Ball valve (general) | XB02 | Check back off/closed | Aux | N2 Sup | Piping | SV60 | CB OFF/CLD | -QM60BG01 | Electrical | 24 VAC | 24 VAC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =A01QJB01&MFB.001
=G01NHA01BZ001 | G01NHA01BZ001-BC01 | =G01NHA01BZ001-BC01;XU01 | ELY1 RECT1 MEAS1 CURR1 GRP FLT | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 1 DC CURRENT MEASUREMENT GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 001 | Measuring System 1 | -BC01 | DC Current Measurement | XU01 | Group fault alarm | Ely1 | Rect1 | Meas1 | Curr1 | GRP FLT | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | IIC | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | EA01 | 01 | =G01NHA01BZ001-BC01&EFS.010 |  |  |  | U012UBB01UC001
=G01NHA01BZ001 | G01NHA01BZ001-FC01 | =G01NHA01BZ001-FC01;XU01 | ELY1 RECT1 MEAS1 24V MON1 GRP FLT | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 1 24VDC DISTRIBUTION GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 001 | Measuring System 1 | -FC01 | 24VDC Distribution | XU01 | Group fault alarm | Ely1 | Rect1 | Meas1 | 24V MON1 | GRP FLT | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | EA | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | EA01 | 02 | =G01NHA01BZ001-FC01&EFS.003 |  |  |  | U012UBB01UC001
=G01NHA01BZ001 | G01NHA01BZ001-TF01 | =G01NHA01BZ001-TF01;XW02 | ELY1 RECT1 MEAS1 DC MON1 WARN CODE | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 1 DC ISOLATION MONITORING ALARM SYSTEM - ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 001 | Measuring System 1 | -TF01 | DC Isolation Monitoring | XW02 | Alarm system - Alarm | Ely1 | Rect1 | Meas1 | DC MON1 | WARN CODE | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | EIS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW02 | EA01 | 04 | =G01NHA01BZ001-TF01&EFS.006 |  |  |  | U012UBB01UC001
=G01NHA01BZ001 | G01NHA01BZ001-TF01 | =G01NHA01BZ001-TF01;XW01 | ELY1 RECT1 MEAS1 DC MON1 AL/FLT CODE | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 1 DC ISOLATION MONITORING ALARM SYSTEM - WARNING | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 001 | Measuring System 1 | -TF01 | DC Isolation Monitoring | XW01 | Alarm system - Warning | Ely1 | Rect1 | Meas1 | DC MON1 | AL/FLT CODE | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | EIS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 03 | =G01NHA01BZ001-TF01&EFS.006 |  |  |  | U012UBB01UC001
=G01NHA01BZ002 | G01NHA01BZ002-BC01 | =G01NHA01BZ002-BC01;XU01 | ELY1 RECT1 MEAS2 CURR1 GRP FLT | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 2 DC CURRENT MEASUREMENT GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 002 | Measuring System 2 | -BC01 | DC Current Measurement | XU01 | Group fault alarm | Ely1 | Rect1 | Meas2 | Curr1 | GRP FLT | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | IIC | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | EA01 | 05 | =G01NHA01BZ002-BC01&EFS.010 |  |  |  | U012UBB01UC001
=G01NHA01BZ002 | G01NHA01BZ002-FC01 | =G01NHA01BZ002-FC01;XU01 | ELY1 RECT1 MEAS2 24V MON1 GRP FLT | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 2 24VDC DISTRIBUTION GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 002 | Measuring System 2 | -FC01 | 24VDC Distribution | XU01 | Group fault alarm | Ely1 | Rect1 | Meas2 | 24V MON1 | GRP FLT | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | EA | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | EA01 | 06 | =G01NHA01BZ002-FC01&EFS.003 |  |  |  | U012UBB01UC001
=G01NHA01BZ002 | G01NHA01BZ002-TF01 | =G01NHA01BZ002-TF01;XW02 | ELY1 RECT1 MEAS2 DC MON1 WARN CODE | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 2 DC ISOLATION MONITORING ALARM SYSTEM - ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 002 | Measuring System 2 | -TF01 | DC Isolation Monitoring | XW02 | Alarm system - Alarm | Ely1 | Rect1 | Meas2 | DC MON1 | WARN CODE | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | EIS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW02 | EA01 | 08 | =G01NHA01BZ002-TF01&EFS.006 |  |  |  | U012UBB01UC001
=G01NHA01BZ002 | G01NHA01BZ002-TF01 | =G01NHA01BZ002-TF01;XW01 | ELY1 RECT1 MEAS2 DC MON1 AL/FLT CODE | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 2 DC ISOLATION MONITORING ALARM SYSTEM - WARNING | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 002 | Measuring System 2 | -TF01 | DC Isolation Monitoring | XW01 | Alarm system - Warning | Ely1 | Rect1 | Meas2 | DC MON1 | AL/FLT CODE | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | EIS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 07 | =G01NHA01BZ002-TF01&EFS.006 |  |  |  | U012UBB01UC001
=G01NHA01BZ003 | G01NHA01BZ003-BC01 | =G01NHA01BZ003-BC01;XU01 | ELY1 RECT1 MEAS3 CURR1 GRP FLT | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 3 DC CURRENT MEASUREMENT GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 003 | Measuring System 3 | -BC01 | DC Current Measurement | XU01 | Group fault alarm | Ely1 | Rect1 | Meas3 | Curr1 | GRP FLT | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | IIC | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | EA01 | 01 | =G01NHA01BZ003-BC01&EFS.010 |  |  |  | U012UBB01UC002
=G01NHA01BZ003 | G01NHA01BZ003-FC01 | =G01NHA01BZ003-FC01;XU01 | ELY1 RECT1 MEAS3 24V MON1 GRP FLT | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 3 24VDC DISTRIBUTION GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 003 | Measuring System 3 | -FC01 | 24VDC Distribution | XU01 | Group fault alarm | Ely1 | Rect1 | Meas3 | 24V MON1 | GRP FLT | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | EA | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | EA01 | 02 | =G01NHA01BZ003-FC01&EFS.003 |  |  |  | U012UBB01UC002
=G01NHA01BZ003 | G01NHA01BZ003-TF01 | =G01NHA01BZ003-TF01;XW02 | ELY1 RECT1 MEAS3 DC MON1 WARN CODE | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 3 DC ISOLATION MONITORING ALARM SYSTEM - ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 003 | Measuring System 3 | -TF01 | DC Isolation Monitoring | XW02 | Alarm system - Alarm | Ely1 | Rect1 | Meas3 | DC MON1 | WARN CODE | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | EIS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW02 | EA01 | 04 | =G01NHA01BZ003-TF01&EFS.006 |  |  |  | U012UBB01UC002
=G01NHA01BZ003 | G01NHA01BZ003-TF01 | =G01NHA01BZ003-TF01;XW01 | ELY1 RECT1 MEAS3 DC MON1 AL/FLT CODE | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 3 DC ISOLATION MONITORING ALARM SYSTEM - WARNING | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 003 | Measuring System 3 | -TF01 | DC Isolation Monitoring | XW01 | Alarm system - Warning | Ely1 | Rect1 | Meas3 | DC MON1 | AL/FLT CODE | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | EIS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 03 | =G01NHA01BZ003-TF01&EFS.006 |  |  |  | U012UBB01UC002
=G01NHA01BZ004 | G01NHA01BZ004-BC01 | =G01NHA01BZ004-BC01;XU01 | ELY1 RECT1 MEAS4 CURR1 GRP FLT | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 4 DC CURRENT MEASUREMENT GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 004 | Measuring System 4 | -BC01 | DC Current Measurement | XU01 | Group fault alarm | Ely1 | Rect1 | Meas4 | Curr1 | GRP FLT | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | IIC | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | EA01 | 05 | =G01NHA01BZ004-BC01&EFS.010 |  |  |  | U012UBB01UC002
=G01NHA01BZ004 | G01NHA01BZ004-FC01 | =G01NHA01BZ004-FC01;XU01 | ELY1 RECT1 MEAS4 24V MON1 GRP FLT | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 4 24VDC DISTRIBUTION GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 004 | Measuring System 4 | -FC01 | 24VDC Distribution | XU01 | Group fault alarm | Ely1 | Rect1 | Meas4 | 24V MON1 | GRP FLT | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | EA | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | EA01 | 06 | =G01NHA01BZ004-FC01&EFS.003 |  |  |  | U012UBB01UC002
=G01NHA01BZ004 | G01NHA01BZ004-TF01 | =G01NHA01BZ004-TF01;XW02 | ELY1 RECT1 MEAS4 DC MON1 WARN CODE | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 4 DC ISOLATION MONITORING ALARM SYSTEM - ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 004 | Measuring System 4 | -TF01 | DC Isolation Monitoring | XW02 | Alarm system - Alarm | Ely1 | Rect1 | Meas4 | DC MON1 | WARN CODE | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | EIS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW02 | EA01 | 08 | =G01NHA01BZ004-TF01&EFS.006 |  |  |  | U012UBB01UC002
=G01NHA01BZ004 | G01NHA01BZ004-TF01 | =G01NHA01BZ004-TF01;XW01 | ELY1 RECT1 MEAS4 DC MON1 AL/FLT CODE | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 MEASURING SYSTEMS MEASURING SYSTEM 4 DC ISOLATION MONITORING ALARM SYSTEM - WARNING | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | BZ | Measuring Systems | 004 | Measuring System 4 | -TF01 | DC Isolation Monitoring | XW01 | Alarm system - Warning | Ely1 | Rect1 | Meas4 | DC MON1 | AL/FLT CODE | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | EIS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 07 | =G01NHA01BZ004-TF01&EFS.006 |  |  |  | U012UBB01UC002
=G01NHA01EQ001 | G01NHA01EQ001-GP01 | =G01NHA01EQ001-GP01;XB13 | ELY1 RECT1 COOL PMP1 CHECK CMD | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 COOLING SYSTEMS RECTIFIER COOLING SYSTEM PUMP, GENERAL CHECK COMMAND | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | EQ | Cooling Systems | 001 | Rectifier Cooling System | -GP01 | Pump, general | XB13 | Check command | Ely1 | Rect1 | Cool | PMP1 | Check CMD | 1 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB13 | EA01 | 09 | =G01NHA01EQ001-GP01&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01EQ001 | G01NHA01EQ001-GP02 | =G01NHA01EQ001-GP02;XB13 | ELY1 RECT1 COOL PMP2 CHECK CMD | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 COOLING SYSTEMS RECTIFIER COOLING SYSTEM PUMP, GENERAL CHECK COMMAND | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | EQ | Cooling Systems | 001 | Rectifier Cooling System | -GP02 | Pump, general | XB13 | Check command | Ely1 | Rect1 | Cool | PMP2 | Check CMD | 1 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB13 | EA01 | 10 | =G01NHA01EQ001-GP02&EFS.002 |  |  |  | U012UBB01UC001
=G01NHA01FA001 | G01NHA01FA001-QA01 | =G01NHA01FA001-QA01;XM01 | ELY1 RECT1 OVERV PROT1 SW1 AL1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 OVERVOLTAGE PROTECTION OVERVOLTAGE PROTECTION 1 CIRCUIT-BREAKER SZ S00, FOR MOTOR PROTECTION INDIVIDUAL ALARMS | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | FA | Overvoltage Protection | 001 | Overvoltage Protection 1 | -QA01 | CIRCUIT-BREAKER SZ S00, FOR MOTOR PROTECTION | XM01 | Individual alarms | Ely1 | Rect1 | OverV Prot1 | Sw1 | AL1 | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XM01 | EA01 | 11 | =G01NHA01FA001-QA01&EFS.002 |  |  |  | U012UBB01UC001
=G01NHA01FA002 | G01NHA01FA002-QA01 | =G01NHA01FA002-QA01;XM01 | ELY1 RECT1 OVERV PROT2 SW1 AL1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 OVERVOLTAGE PROTECTION OVERVOLTAGE PROTECTION 2 CIRCUIT-BREAKER SZ S00, FOR MOTOR PROTECTION INDIVIDUAL ALARMS | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | FA | Overvoltage Protection | 002 | Overvoltage Protection 2 | -QA01 | CIRCUIT-BREAKER SZ S00, FOR MOTOR PROTECTION | XM01 | Individual alarms | Ely1 | Rect1 | OverV Prot2 | Sw1 | AL1 | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XM01 | EA01 | 12 | =G01NHA01FA002-QA01&EFS.002 |  |  |  | U012UBB01UC001
=G01NHA01FA003 | G01NHA01FA003-QA01 | =G01NHA01FA003-QA01;XM01 | ELY1 RECT1 OVERV PROT3 SW1 AL1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 OVERVOLTAGE PROTECTION OVERVOLTAGE PROTECTION 3 CIRCUIT-BREAKER SZ S00, FOR MOTOR PROTECTION INDIVIDUAL ALARMS | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | FA | Overvoltage Protection | 003 | Overvoltage Protection 3 | -QA01 | CIRCUIT-BREAKER SZ S00, FOR MOTOR PROTECTION | XM01 | Individual alarms | Ely1 | Rect1 | OverV Prot3 | Sw1 | AL1 | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XM01 | EA01 | 09 | =G01NHA01FA003-QA01&EFS.002 |  |  |  | U012UBB01UC002
=G01NHA01FA004 | G01NHA01FA004-QA01 | =G01NHA01FA004-QA01;XM01 | ELY1 RECT1 OVERV PROT4 SW1 AL1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 OVERVOLTAGE PROTECTION OVERVOLTAGE PROTECTION 4 CIRCUIT-BREAKER SZ S00, FOR MOTOR PROTECTION INDIVIDUAL ALARMS | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | FA | Overvoltage Protection | 004 | Overvoltage Protection 4 | -QA01 | CIRCUIT-BREAKER SZ S00, FOR MOTOR PROTECTION | XM01 | Individual alarms | Ely1 | Rect1 | OverV Prot4 | Sw1 | AL1 | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XM01 | EA01 | 10 | =G01NHA01FA004-QA01&EFS.002 |  |  |  | U012UBB01UC002
=G01NHA01KF001 | G01NHA01KF001-BA11 | =G01NHA01KF001-BA11;XB01 | ELY1 RECT1 CTRL U1 400VAC MON CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 400VAC MONITORING CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -BA11 | 400VAC Monitoring | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 400VAC MON | CB ON/OPN | 1 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 13 | =G01NHA01KF001-BA11&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-BA21 | =G01NHA01KF001-BA21;XB01 | ELY1 RECT1 CTRL U1 230VAC MON CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 230VAC MONITORING CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -BA21 | 230VAC Monitoring | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 230VAC MON | CB ON/OPN | 1 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 14 | =G01NHA01KF001-BA21&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-BA41 | =G01NHA01KF001-BA41;XB01 | ELY1 RECT1 CTRL U1 UPS MON CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 230VAC UPS MONITORING CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -BA41 | 230VAC UPS Monitoring | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | UPS MON | CB ON/OPN | 1 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 15 | =G01NHA01KF001-BA41&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-FC01 | =G01NHA01KF001-FC01;XB01 | ELY1 RECT1 CTRL U1 24V MON1 CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 24VDC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -FC01 | 24VDC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 24V MON1 | CB ON/OPN | -FC01 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 16 | =G01NHA01KF001-FC01&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-FC02 | =G01NHA01KF001-FC02;XB01 | ELY1 RECT1 CTRL U1 24V MON2 CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 24VDC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -FC02 | 24VDC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 24V MON2 | CB ON/OPN | -FC02 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 01 | =G01NHA01KF001-FC02&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-FC03 | =G01NHA01KF001-FC03;XB01 | ELY1 RECT1 CTRL U1 24V MON3 CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 24VDC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -FC03 | 24VDC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 24V MON3 | CB ON/OPN | -FC03 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 02 | =G01NHA01KF001-FC03&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-FC11 | =G01NHA01KF001-FC11;XB01 | ELY1 RECT1 CTRL U1 400VAC IN CB ON/OPN | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 400VAC INPUT CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -FC11 | 400VAC Input | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 400VAC In | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 03 | =G01NHA01KF001-FC11&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-FC21 | =G01NHA01KF001-FC21;XB01 | ELY1 RECT1 CTRL U1 230VAC1 CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -FC21 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 230VAC1 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 04 | =G01NHA01KF001-FC21&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-FC22 | =G01NHA01KF001-FC22;XB01 | ELY1 RECT1 CTRL U1 230VAC2 CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -FC22 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 230VAC2 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 05 | =G01NHA01KF001-FC22&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-FC23 | =G01NHA01KF001-FC23;XB01 | ELY1 RECT1 CTRL U1 230VAC3 CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -FC23 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 230VAC3 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 06 | =G01NHA01KF001-FC23&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-FC24 | =G01NHA01KF001-FC24;XB01 | ELY1 RECT1 CTRL U1 230VAC4 CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -FC24 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 230VAC4 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 07 | =G01NHA01KF001-FC24&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-FC25 | =G01NHA01KF001-FC25;XB01 | ELY1 RECT1 CTRL U1 230VAC5 CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -FC25 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 230VAC5 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 08 | =G01NHA01KF001-FC25&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-FC26 | =G01NHA01KF001-FC26;XB01 | ELY1 RECT1 CTRL U1 230VAC6 CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -FC26 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 230VAC6 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 09 | =G01NHA01KF001-FC26&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-FC27 | =G01NHA01KF001-FC27;XB01 | ELY1 RECT1 CTRL U1 230VAC7 CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -FC27 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 230VAC7 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 10 | =G01NHA01KF001-FC27&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-FC28 | =G01NHA01KF001-FC28;XB01 | ELY1 RECT1 CTRL U1 230VAC8 CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -FC28 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 230VAC8 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 11 | =G01NHA01KF001-FC28&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-FC29 | =G01NHA01KF001-FC29;XB01 | ELY1 RECT1 CTRL U1 230VAC9 CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -FC29 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 230VAC9 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 12 | =G01NHA01KF001-FC29&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-FC30 | =G01NHA01KF001-FC30;XB01 | ELY1 RECT1 CTRL U1 230VAC10 CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -FC30 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 230VAC10 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 13 | =G01NHA01KF001-FC30&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-FC31 | =G01NHA01KF001-FC31;XB01 | ELY1 RECT1 CTRL U1 230VAC11 CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -FC31 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 230VAC11 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 14 | =G01NHA01KF001-FC31&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-FC41 | =G01NHA01KF001-FC41;XB01 | ELY1 RECT1 CTRL U1 230VAC UPS1 CB ON/OPN | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -FC41 | 230VAC UPS Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 230VAC UPS1 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 15 | =G01NHA01KF001-FC41&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-FC42 | =G01NHA01KF001-FC42;XB01 | ELY1 RECT1 CTRL U1 230VAC UPS2 CB ON/OPN | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -FC42 | 230VAC UPS Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 230VAC UPS2 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 16 | =G01NHA01KF001-FC42&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-FC43 | =G01NHA01KF001-FC43;XB01 | ELY1 RECT1 CTRL U1 230VAC UPS3 CB ON/OPN | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -FC43 | 230VAC UPS Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 230VAC UPS3 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 01 | =G01NHA01KF001-FC43&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-QA11 | =G01NHA01KF001-QA11;XB01 | ELY1 RECT1 CTRL U1 SW 400VAC1 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -QA11 | 400VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | Sw 400VAC1 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 02 | =G01NHA01KF001-QA11&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-QA12 | =G01NHA01KF001-QA12;XB01 | ELY1 RECT1 CTRL U1 SW 400VAC2 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -QA12 | 400VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | Sw 400VAC2 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 03 | =G01NHA01KF001-QA12&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-QA13 | =G01NHA01KF001-QA13;XB01 | ELY1 RECT1 CTRL U1 SW 400VAC3 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -QA13 | 400VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | Sw 400VAC3 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 04 | =G01NHA01KF001-QA13&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-QA14 | =G01NHA01KF001-QA14;XB01 | ELY1 RECT1 CTRL U1 SW 400VAC4 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -QA14 | 400VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | Sw 400VAC4 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 05 | =G01NHA01KF001-QA14&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-QA15 | =G01NHA01KF001-QA15;XB01 | ELY1 RECT1 CTRL U1 SW 400VAC5 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -QA15 | 400VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | Sw 400VAC5 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 06 | =G01NHA01KF001-QA15&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-QA16 | =G01NHA01KF001-QA16;XB01 | ELY1 RECT1 CTRL U1 SW 400VAC6 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -QA16 | 400VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | Sw 400VAC6 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 07 | =G01NHA01KF001-QA16&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-QA17 | =G01NHA01KF001-QA17;XB01 | ELY1 RECT1 CTRL U1 SW 400VAC7 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -QA17 | 400VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | Sw 400VAC7 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 08 | =G01NHA01KF001-QA17&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-QA18 | =G01NHA01KF001-QA18;XB01 | ELY1 RECT1 CTRL U1 SW 400VAC8 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -QA18 | 400VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | Sw 400VAC8 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 09 | =G01NHA01KF001-QA18&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-SF01 | =G01NHA01KF001-SF01;XW02 | ELY1 RECT1 CTRL U1 SW OFF WARN CODE | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 EMERGENCY STOP - PUSHBUTTON - I&C CABINET 1 RECTIFIER SYSTEM COMPONENT PROTECTION | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -SF01 | Emergency Stop - Pushbutton - I&C Cabinet 1 Rectifier System | XW02 | Component protection | Ely1 | Rect1 | CTRL U1 | Sw OFF | WARN CODE | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHA01KF001+U012UBB01UC001-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | B10:XW02 | XW02 | 13 | =G01NHA01KF001-SF01&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-SF01 | =G01NHA01KF001-SF01;XW01 | ELY1 RECT1 CTRL U1 SW OFF AL/FLT CODE | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 EMERGENCY STOP - PUSHBUTTON - I&C CABINET 1 RECTIFIER SYSTEM COMPONENT PROTECTION | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -SF01 | Emergency Stop - Pushbutton - I&C Cabinet 1 Rectifier System | XW01 | Component protection | Ely1 | Rect1 | CTRL U1 | Sw OFF | AL/FLT CODE | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHA01KF001+U012UBB01UC001-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | B10:XW01 | XW01 | 01 | =G01NHA01KF001-SF01&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-TB01 | =G01NHA01KF001-TB01;XB01 | ELY1 RECT1 CTRL U1 24VDC MON1 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 SITOP PSU6200 24 V/20 A CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -TB01 | SITOP PSU6200 24 V/20 A | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 24VDC MON1 | CB ON/OPN | -TB01 | Electrical | 24 VDC | 24 VDC | Wire | Continuous signal |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 10 | =G01NHA01KF001-TB01&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF001 | G01NHA01KF001-TB02 | =G01NHA01KF001-TB02;XB01 | ELY1 RECT1 CTRL U1 24VDC MON2 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 1 - RECTIFIER SYSTEM 1 SITOP PSU6200 24 V/20 A CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 001 | I&C Cabinet 1 - Rectifier System 1 | -TB02 | SITOP PSU6200 24 V/20 A | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U1 | 24VDC MON2 | CB ON/OPN | -TB02 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 11 | =G01NHA01KF001-TB02&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01KF002 | G01NHA01KF002-BA11 | =G01NHA01KF002-BA11;XB01 | ELY1 RECT1 CTRL U2 400VAC MON CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 400VAC MONITORING CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -BA11 | 400VAC Monitoring | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 400VAC MON | CB ON/OPN | 1 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 11 | =G01NHA01KF002-BA11&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-BA21 | =G01NHA01KF002-BA21;XB01 | ELY1 RECT1 CTRL U2 230VAC MON CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 230VAC MONITORING CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -BA21 | 230VAC Monitoring | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 230VAC MON | CB ON/OPN | 1 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 12 | =G01NHA01KF002-BA21&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-BA41 | =G01NHA01KF002-BA41;XB01 | ELY1 RECT1 CTRL U2 UPS MON CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 230VAC UPS MONITORING CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -BA41 | 230VAC UPS Monitoring | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | UPS MON | CB ON/OPN | 1 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 13 | =G01NHA01KF002-BA41&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-FC01 | =G01NHA01KF002-FC01;XB01 | ELY1 RECT1 CTRL U2 24V MON1 CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 24VDC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -FC01 | 24VDC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 24V MON1 | CB ON/OPN | -FC01 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 14 | =G01NHA01KF002-FC01&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-FC02 | =G01NHA01KF002-FC02;XB01 | ELY1 RECT1 CTRL U2 24V MON2 CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 24VDC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -FC02 | 24VDC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 24V MON2 | CB ON/OPN | -FC02 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 15 | =G01NHA01KF002-FC02&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-FC03 | =G01NHA01KF002-FC03;XB01 | ELY1 RECT1 CTRL U2 24V MON3 CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 24VDC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -FC03 | 24VDC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 24V MON3 | CB ON/OPN | -FC03 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 16 | =G01NHA01KF002-FC03&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-FC11 | =G01NHA01KF002-FC11;XB01 | ELY1 RECT1 CTRL U2 400VAC IN CB ON/OPN | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 400VAC INPUT CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -FC11 | 400VAC Input | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 400VAC In | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 01 | =G01NHA01KF002-FC11&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-FC21 | =G01NHA01KF002-FC21;XB01 | ELY1 RECT1 CTRL U2 230VAC1 CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -FC21 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 230VAC1 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 02 | =G01NHA01KF002-FC21&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-FC22 | =G01NHA01KF002-FC22;XB01 | ELY1 RECT1 CTRL U2 230VAC2 CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -FC22 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 230VAC2 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 03 | =G01NHA01KF002-FC22&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-FC23 | =G01NHA01KF002-FC23;XB01 | ELY1 RECT1 CTRL U2 230VAC3 CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -FC23 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 230VAC3 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 04 | =G01NHA01KF002-FC23&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-FC24 | =G01NHA01KF002-FC24;XB01 | ELY1 RECT1 CTRL U2 230VAC4 CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -FC24 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 230VAC4 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 05 | =G01NHA01KF002-FC24&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-FC25 | =G01NHA01KF002-FC25;XB01 | ELY1 RECT1 CTRL U2 230VAC5 CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -FC25 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 230VAC5 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 06 | =G01NHA01KF002-FC25&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-FC26 | =G01NHA01KF002-FC26;XB01 | ELY1 RECT1 CTRL U2 230VAC6 CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -FC26 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 230VAC6 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 07 | =G01NHA01KF002-FC26&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-FC27 | =G01NHA01KF002-FC27;XB01 | ELY1 RECT1 CTRL U2 230VAC7 CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -FC27 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 230VAC7 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 08 | =G01NHA01KF002-FC27&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-FC28 | =G01NHA01KF002-FC28;XB01 | ELY1 RECT1 CTRL U2 230VAC8 CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -FC28 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 230VAC8 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 09 | =G01NHA01KF002-FC28&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-FC29 | =G01NHA01KF002-FC29;XB01 | ELY1 RECT1 CTRL U2 230VAC9 CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -FC29 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 230VAC9 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 10 | =G01NHA01KF002-FC29&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-FC30 | =G01NHA01KF002-FC30;XB01 | ELY1 RECT1 CTRL U2 230VAC10 CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -FC30 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 230VAC10 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 11 | =G01NHA01KF002-FC30&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-FC31 | =G01NHA01KF002-FC31;XB01 | ELY1 RECT1 CTRL U2 230VAC11 CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -FC31 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 230VAC11 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 12 | =G01NHA01KF002-FC31&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-FC41 | =G01NHA01KF002-FC41;XB01 | ELY1 RECT1 CTRL U2 230VAC UPS1 CB ON/OPN | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -FC41 | 230VAC UPS Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 230VAC UPS1 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 13 | =G01NHA01KF002-FC41&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-FC42 | =G01NHA01KF002-FC42;XB01 | ELY1 RECT1 CTRL U2 230VAC UPS2 CB ON/OPN | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -FC42 | 230VAC UPS Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 230VAC UPS2 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 14 | =G01NHA01KF002-FC42&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-FC43 | =G01NHA01KF002-FC43;XB01 | ELY1 RECT1 CTRL U2 230VAC UPS3 CB ON/OPN | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -FC43 | 230VAC UPS Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 230VAC UPS3 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 15 | =G01NHA01KF002-FC43&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-QA11 | =G01NHA01KF002-QA11;XB01 | ELY1 RECT1 CTRL U2 SW 400VAC1 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -QA11 | 400VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | Sw 400VAC1 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 16 | =G01NHA01KF002-QA11&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-QA12 | =G01NHA01KF002-QA12;XB01 | ELY1 RECT1 CTRL U2 SW 400VAC2 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -QA12 | 400VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | Sw 400VAC2 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 01 | =G01NHA01KF002-QA12&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-QA13 | =G01NHA01KF002-QA13;XB01 | ELY1 RECT1 CTRL U2 SW 400VAC3 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -QA13 | 400VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | Sw 400VAC3 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 02 | =G01NHA01KF002-QA13&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-QA14 | =G01NHA01KF002-QA14;XB01 | ELY1 RECT1 CTRL U2 SW 400VAC4 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -QA14 | 400VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | Sw 400VAC4 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 03 | =G01NHA01KF002-QA14&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-QA15 | =G01NHA01KF002-QA15;XB01 | ELY1 RECT1 CTRL U2 SW 400VAC5 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -QA15 | 400VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | Sw 400VAC5 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 04 | =G01NHA01KF002-QA15&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-QA16 | =G01NHA01KF002-QA16;XB01 | ELY1 RECT1 CTRL U2 SW 400VAC6 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -QA16 | 400VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | Sw 400VAC6 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 05 | =G01NHA01KF002-QA16&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-QA17 | =G01NHA01KF002-QA17;XB01 | ELY1 RECT1 CTRL U2 SW 400VAC7 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -QA17 | 400VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | Sw 400VAC7 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 06 | =G01NHA01KF002-QA17&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-QA18 | =G01NHA01KF002-QA18;XB01 | ELY1 RECT1 CTRL U2 SW 400VAC8 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -QA18 | 400VAC Distribution | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | Sw 400VAC8 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 07 | =G01NHA01KF002-QA18&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-TB01 | =G01NHA01KF002-TB01;XB01 | ELY1 RECT1 CTRL U2 24VDC MON1 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 SITOP PSU6200 24 V/20 A CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -TB01 | SITOP PSU6200 24 V/20 A | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 24VDC MON1 | CB ON/OPN | -TB01 | Electrical | 24 VDC | 24 VDC | Wire | Continuous signal |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 08 | =G01NHA01KF002-TB01&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01KF002 | G01NHA01KF002-TB02 | =G01NHA01KF002-TB02;XB01 | ELY1 RECT1 CTRL U2 24VDC MON2 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 CONTROL UNITS I&C CABINET 2 - RECTIFIER SYSTEM 1 SITOP PSU6200 24 V/20 A CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | KF | Control Units | 002 | I&C Cabinet 2 - Rectifier System 1 | -TB02 | SITOP PSU6200 24 V/20 A | XB01 | Check back on/open | Ely1 | Rect1 | CTRL U2 | 24VDC MON2 | CB ON/OPN | -TB02 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 09 | =G01NHA01KF002-TB02&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01QZ001 | G01NHA01QZ001-QB01 | =G01NHA01QZ001-QB01;XB01 | ELY1 RECT1 DC SWG1 DISC DC+ CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 1 DISCONNECTOR - DC+ CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 001 | DC-Switchgear 1 | -QB01 | Disconnector - DC+ | XB01 | Check back on/open | Ely1 | Rect1 | DC Swg1 | Disc DC+ | CB ON/OPN | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:003 | 5 | 02 | =G01NHA01QZ001-QB01&EFS.005 |  |  |  | U012UBB01UC001
=G01NHA01QZ001 | G01NHA01QZ001-QB01 | =G01NHA01QZ001-QB01;XB02 | ELY1 RECT1 DC SWG1 DISC DC+ CB OFF/CLD | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 1 DISCONNECTOR - DC+ CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 001 | DC-Switchgear 1 | -QB01 | Disconnector - DC+ | XB02 | Check back off/closed | Ely1 | Rect1 | DC Swg1 | Disc DC+ | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:004 | 7 | 14 | =G01NHA01QZ001-QB01&EFS.005 |  |  |  | U012UBB01UC001
=G01NHA01QZ001 | G01NHA01QZ001-QB02 | =G01NHA01QZ001-QB02;XB01 | ELY1 RECT1 DC SWG1 DISC DC- CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 1 DISCONNECTOR - DC- CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 001 | DC-Switchgear 1 | -QB02 | Disconnector - DC- | XB01 | Check back on/open | Ely1 | Rect1 | DC Swg1 | Disc DC- | CB ON/OPN | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:007 | 14 | 03 | =G01NHA01QZ001-QB02&EFS.005 |  |  |  | U012UBB01UC001
=G01NHA01QZ001 | G01NHA01QZ001-QB02 | =G01NHA01QZ001-QB02;XB02 | ELY1 RECT1 DC SWG1 DISC DC- CB OFF/CLD | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 1 DISCONNECTOR - DC- CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 001 | DC-Switchgear 1 | -QB02 | Disconnector - DC- | XB02 | Check back off/closed | Ely1 | Rect1 | DC Swg1 | Disc DC- | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:008 | 15 | 15 | =G01NHA01QZ001-QB02&EFS.005 |  |  |  | U012UBB01UC001
=G01NHA01QZ002 | G01NHA01QZ002-QB01 | =G01NHA01QZ002-QB01;XB01 | ELY1 RECT1 DC SWG2 DISC DC+ CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 2 DISCONNECTOR - DC+ CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 002 | DC-Switchgear 2 | -QB01 | Disconnector - DC+ | XB01 | Check back on/open | Ely1 | Rect1 | DC Swg2 | Disc DC+ | CB ON/OPN | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:003 | 6 | 04 | =G01NHA01QZ002-QB01&EFS.005 |  |  |  | U012UBB01UC001
=G01NHA01QZ002 | G01NHA01QZ002-QB01 | =G01NHA01QZ002-QB01;XB02 | ELY1 RECT1 DC SWG2 DISC DC+ CB OFF/CLD | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 2 DISCONNECTOR - DC+ CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 002 | DC-Switchgear 2 | -QB01 | Disconnector - DC+ | XB02 | Check back off/closed | Ely1 | Rect1 | DC Swg2 | Disc DC+ | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:004 | 7 | 16 | =G01NHA01QZ002-QB01&EFS.005 |  |  |  | U012UBB01UC001
=G01NHA01QZ002 | G01NHA01QZ002-QB02 | =G01NHA01QZ002-QB02;XB01 | ELY1 RECT1 DC SWG2 DISC DC- CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 2 DISCONNECTOR - DC- CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 002 | DC-Switchgear 2 | -QB02 | Disconnector - DC- | XB01 | Check back on/open | Ely1 | Rect1 | DC Swg2 | Disc DC- | CB ON/OPN | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:007 | 14 | 05 | =G01NHA01QZ002-QB02&EFS.005 |  |  |  | U012UBB01UC001
=G01NHA01QZ002 | G01NHA01QZ002-QB02 | =G01NHA01QZ002-QB02;XB02 | ELY1 RECT1 DC SWG2 DISC DC- CB OFF/CLD | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 2 DISCONNECTOR - DC- CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 002 | DC-Switchgear 2 | -QB02 | Disconnector - DC- | XB02 | Check back off/closed | Ely1 | Rect1 | DC Swg2 | Disc DC- | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:008 | 15 | 17 | =G01NHA01QZ002-QB02&EFS.005 |  |  |  | U012UBB01UC001
=G01NHA01QZ003 | G01NHA01QZ003-QB01 | =G01NHA01QZ003-QB01;XB01 | ELY1 RECT1 DC SWG3 DISC DC+ CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 3 DISCONNECTOR - DC+ CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 003 | DC-Switchgear 3 | -QB01 | Disconnector - DC+ | XB01 | Check back on/open | Ely1 | Rect1 | DC Swg3 | Disc DC+ | CB ON/OPN | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes |  | =G01NHA01KF002+U012UBB01UC002-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:003 | 6 | 01 | =G01NHA01QZ003-QB01&EFS.005 |  |  |  | U012UBB01UC002
=G01NHA01QZ003 | G01NHA01QZ003-QB01 | =G01NHA01QZ003-QB01;XB02 | ELY1 RECT1 DC SWG3 DISC DC+ CB OFF/CLD | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 3 DISCONNECTOR - DC+ CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 003 | DC-Switchgear 3 | -QB01 | Disconnector - DC+ | XB02 | Check back off/closed | Ely1 | Rect1 | DC Swg3 | Disc DC+ | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes |  | =G01NHA01KF002+U012UBB01UC002-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:004 | 7 | 13 | =G01NHA01QZ003-QB01&EFS.005 |  |  |  | U012UBB01UC002
=G01NHA01QZ003 | G01NHA01QZ003-QB02 | =G01NHA01QZ003-QB02;XB01 | ELY1 RECT1 DC SWG3 DISC DC- CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 3 DISCONNECTOR - DC- CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 003 | DC-Switchgear 3 | -QB02 | Disconnector - DC- | XB01 | Check back on/open | Ely1 | Rect1 | DC Swg3 | Disc DC- | CB ON/OPN | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes |  | =G01NHA01KF002+U012UBB01UC002-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:007 | 13 | 02 | =G01NHA01QZ003-QB02&EFS.005 |  |  |  | U012UBB01UC002
=G01NHA01QZ003 | G01NHA01QZ003-QB02 | =G01NHA01QZ003-QB02;XB02 | ELY1 RECT1 DC SWG3 DISC DC- CB OFF/CLD | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 3 DISCONNECTOR - DC- CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 003 | DC-Switchgear 3 | -QB02 | Disconnector - DC- | XB02 | Check back off/closed | Ely1 | Rect1 | DC Swg3 | Disc DC- | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes |  | =G01NHA01KF002+U012UBB01UC002-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:008 | 15 | 14 | =G01NHA01QZ003-QB02&EFS.005 |  |  |  | U012UBB01UC002
=G01NHA01QZ004 | G01NHA01QZ004-QB01 | =G01NHA01QZ004-QB01;XB01 | ELY1 RECT1 DC SWG4 DISC DC+ CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 4 DISCONNECTOR - DC+ CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 004 | DC-Switchgear 4 | -QB01 | Disconnector - DC+ | XB01 | Check back on/open | Ely1 | Rect1 | DC Swg4 | Disc DC+ | CB ON/OPN | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes |  | =G01NHA01KF002+U012UBB01UC002-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:003 | 6 | 03 | =G01NHA01QZ004-QB01&EFS.005 |  |  |  | U012UBB01UC002
=G01NHA01QZ004 | G01NHA01QZ004-QB01 | =G01NHA01QZ004-QB01;XB02 | ELY1 RECT1 DC SWG4 DISC DC+ CB OFF/CLD | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 4 DISCONNECTOR - DC+ CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 004 | DC-Switchgear 4 | -QB01 | Disconnector - DC+ | XB02 | Check back off/closed | Ely1 | Rect1 | DC Swg4 | Disc DC+ | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes |  | =G01NHA01KF002+U012UBB01UC002-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:004 | 7 | 15 | =G01NHA01QZ004-QB01&EFS.005 |  |  |  | U012UBB01UC002
=G01NHA01QZ004 | G01NHA01QZ004-QB02 | =G01NHA01QZ004-QB02;XB01 | ELY1 RECT1 DC SWG4 DISC DC- CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 4 DISCONNECTOR - DC- CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 004 | DC-Switchgear 4 | -QB02 | Disconnector - DC- | XB01 | Check back on/open | Ely1 | Rect1 | DC Swg4 | Disc DC- | CB ON/OPN | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes |  | =G01NHA01KF002+U012UBB01UC002-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:007 | 13 | 04 | =G01NHA01QZ004-QB02&EFS.005 |  |  |  | U012UBB01UC002
=G01NHA01QZ004 | G01NHA01QZ004-QB02 | =G01NHA01QZ004-QB02;XB02 | ELY1 RECT1 DC SWG4 DISC DC- CB OFF/CLD | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 4 DISCONNECTOR - DC- CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 004 | DC-Switchgear 4 | -QB02 | Disconnector - DC- | XB02 | Check back off/closed | Ely1 | Rect1 | DC Swg4 | Disc DC- | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes |  | =G01NHA01KF002+U012UBB01UC002-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:007 | 14 | 16 | =G01NHA01QZ004-QB02&EFS.005 |  |  |  | U012UBB01UC002
=G01NHA01RA001 | G01NHA01RA001-KF01 | =G01NHA01RA001-KF01;XB13 | ELY1 RECT1 DISCH RES1 OUTP MOD CHECK CMD | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RESISTORS DISCHARGE-RESISTOR 1 OUTPUT COUPLER RELAY COUPLER, 1 CHANGE-OVER CONTACT CHECK COMMAND | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | RA | Resistors | 001 | Discharge-Resistor 1 | -KF01 | Output coupler Relay coupler, 1 change-over contact | XB13 | Check command | Ely1 | Rect1 | Disch Res1 | Outp Mod | Check CMD | -XG01 | Electrical |  |  |  | Undefined |  |  | DI | 0 | GS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB13 | EA01 | 04 | =G01NHA01RA001-KF01&EFS.004 |  |  |  | U012UBB01UC001
=G01NHA01RA002 | G01NHA01RA002-KF01 | =G01NHA01RA002-KF01;XB13 | ELY1 RECT1 DISCH RES2 OUTP MOD CHECK CMD | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RESISTORS DISCHARGE-RESISTOR 2 OUTPUT COUPLER RELAY COUPLER, 1 CHANGE-OVER CONTACT CHECK COMMAND | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | RA | Resistors | 002 | Discharge-Resistor 2 | -KF01 | Output coupler Relay coupler, 1 change-over contact | XB13 | Check command | Ely1 | Rect1 | Disch Res2 | Outp Mod | Check CMD | -XG01 | Electrical |  |  |  | Undefined |  |  | DI | 0 | GS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB13 | EA01 | 05 | =G01NHA01RA002-KF01&EFS.004 |  |  |  | U012UBB01UC001
=G01NHA01RA003 | G01NHA01RA003-KF01 | =G01NHA01RA003-KF01;XB13 | ELY1 RECT1 DISCH RES3 OUTP MOD CHECK CMD | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RESISTORS DISCHARGE-RESISTOR 3 OUTPUT COUPLER RELAY COUPLER, 1 CHANGE-OVER CONTACT CHECK COMMAND | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | RA | Resistors | 003 | Discharge-Resistor 3 | -KF01 | Output coupler Relay coupler, 1 change-over contact | XB13 | Check command | Ely1 | Rect1 | Disch Res3 | Outp Mod | Check CMD | -XG01 | Electrical |  |  |  | Undefined |  |  | DI | 0 | GS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB13 | EA01 | 10 | =G01NHA01RA003-KF01&EFS.004 |  |  |  | U012UBB01UC002
=G01NHA01RA004 | G01NHA01RA004-KF01 | =G01NHA01RA004-KF01;XB13 | ELY1 RECT1 DISCH RES4 OUTP MOD CHECK CMD | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RESISTORS DISCHARGE-RESISTOR 4 OUTPUT COUPLER RELAY COUPLER, 1 CHANGE-OVER CONTACT CHECK COMMAND | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | RA | Resistors | 004 | Discharge-Resistor 4 | -KF01 | Output coupler Relay coupler, 1 change-over contact | XB13 | Check command | Ely1 | Rect1 | Disch Res4 | Outp Mod | Check CMD | -XG01 | Electrical |  |  |  | Undefined |  |  | DI | 0 | GS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB13 | EA01 | 11 | =G01NHA01RA004-KF01&EFS.004 |  |  |  | U012UBB01UC002
=G01NHA01TA001 | G01NHA01TA001-BF01 | =G01NHA01TA001-BF01;XM01 | ELY1 RECT1 TRAFO1 FLOW1 AL1 | 27 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER FLOWMETER - OIL CIRCULATION ALARM - OIL FLOWMETER | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BF01 | Flowmeter - Oil Circulation | XM01 | Alarm - Oil Flowmeter | Ely1 | Rect1 | Trafo1 | Flow1 | AL1 | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | FS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XM01 | EA01 | 12 | =G01NHA01TA001-BF01&EFS.014 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-BF02 | =G01NHA01TA001-BF02;XM01 | ELY1 RECT1 TRAFO1 FLOW2 AL1 | 27 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER FLOWMETER - COOLING WATER ALARM - COOLING WATER - FLOWMETER | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BF02 | Flowmeter - Cooling Water | XM01 | Alarm - Cooling Water - Flowmeter | Ely1 | Rect1 | Trafo1 | Flow2 | AL1 | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | FS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XM01 | EA01 | 13 | =G01NHA01TA001-BF02&EFS.015 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-BL01 | =G01NHA01TA001-BL01;XM01 | ELY1 RECT1 TRAFO1 LVL1 AL1 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER LEVEL LIMIT SWITCH - TRANSFORMER OIL LEVEL LEVEL MIN - TRANSFORMER OIL LEVEL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BL01 | Level limit switch - Transformer Oil Level | XM01 | Level Min - Transformer oil level | Ely1 | Rect1 | Trafo1 | Lvl1 | AL1 | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | LS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XM01 | EA01 | 14 | =G01NHA01TA001-BL01&EFS.009 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-BL01 | =G01NHA01TA001-BL01;XM02 | ELY1 RECT1 TRAFO1 LVL1 AL2 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER LEVEL LIMIT SWITCH - TRANSFORMER OIL LEVEL LEVEL MAX - TRANSFORMER OIL LEVEL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BL01 | Level limit switch - Transformer Oil Level | XM02 | Level Max - Transformer oil level | Ely1 | Rect1 | Trafo1 | Lvl1 | AL2 | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | LS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XM02 | EA01 | 15 | =G01NHA01TA001-BL01&EFS.009 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-BL02 | =G01NHA01TA001-BL02;XM01 | ELY1 RECT1 TRAFO1 LVL2 AL1 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER LEVEL LIMIT SWITCH - TRANSFORMER LEAKAGE ALARM - LEVEL LIMIT SWITCH - LEACKAGE TRANSFORMER | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BL02 | Level limit switch - Transformer Leakage | XM01 | Alarm - Level limit switch - Leackage transformer | Ely1 | Rect1 | Trafo1 | Lvl2 | AL1 | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | LS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XM01 | EA01 | 16 | =G01NHA01TA001-BL02&EFS.016 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-BL03 | =G01NHA01TA001-BL03;XM01 | ELY1 RECT1 TRAFO1 LVL3 AL1 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER LEVEL LIMIT SWITCH - TAP CHANGER OIL LEVEL LEVEL MIN - TAP CHANGER OIL LEVEL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BL03 | Level limit switch - Tap Changer Oil Level | XM01 | Level Min - Tap Changer oil level | Ely1 | Rect1 | Trafo1 | Lvl3 | AL1 | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | LS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XM01 | EA01 | 01 | =G01NHA01TA001-BL03&EFS.006 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-BL03 | =G01NHA01TA001-BL03;XM02 | ELY1 RECT1 TRAFO1 LVL3 AL2 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER LEVEL LIMIT SWITCH - TAP CHANGER OIL LEVEL LEVEL MAX - TAP CHANGER OIL LEVEL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BL03 | Level limit switch - Tap Changer Oil Level | XM02 | Level Max - Tap Changer oil level | Ely1 | Rect1 | Trafo1 | Lvl3 | AL2 | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | LS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XM02 | EA01 | 02 | =G01NHA01TA001-BL03&EFS.006 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-BP01 | =G01NHA01TA001-BP01;XM02 | ELY1 RECT1 TRAFO1 PRES1 AL2 | 27 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER PRESSURE SWITCH - TRANSFORMER TRIPPING - PRESSURE SWITCH | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BP01 | Pressure switch - Transformer | XM02 | Tripping - Pressure switch | Ely1 | Rect1 | Trafo1 | Pres1 | AL2 | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | XZ | [13 empty] | Yes | [6 empty] | =G01NHA01TA001-BP01&EFS.001
=G01NHA01TA001 | G01NHA01TA001-BP01 | =G01NHA01TA001-BP01;XM01 | ELY1 RECT1 TRAFO1 PRES1 AL1 | 27 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER PRESSURE SWITCH - TRANSFORMER WARNING - PRESSURE SWITCH | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BP01 | Pressure switch - Transformer | XM01 | Warning - Pressure switch | Ely1 | Rect1 | Trafo1 | Pres1 | AL1 | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | XZ | [13 empty] | Yes |  |  |  | B10:XM01 | EA01 |  | =G01NHA01TA001-BP01&EFS.001
=G01NHA01TA001 | G01NHA01TA001-BT01 | =G01NHA01TA001-BT01;XM02 | ELY1 RECT1 TRAFO1 TEMP1 AL2 | 27 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER TEMPERATURE SWITCH - OIL TEMPERATURE TRIPPING - OIL TEMPERATURE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BT01 | Temperature switch - Oil temperature | XM02 | Tripping - Oil temperature | Ely1 | Rect1 | Trafo1 | Temp1 | AL2 | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | TI | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG12:23 | 23B | 06 | =G01NHA01TA001-BT01&EFS.011 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-BT01 | =G01NHA01TA001-BT01;XM01 | ELY1 RECT1 TRAFO1 TEMP1 AL1 | 27 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER TEMPERATURE SWITCH - OIL TEMPERATURE WARNING - OIL TEMPERATURE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BT01 | Temperature switch - Oil temperature | XM01 | Warning - Oil temperature | Ely1 | Rect1 | Trafo1 | Temp1 | AL1 | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | TI | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XM01 | EA01 | 03 | =G01NHA01TA001-BT01&EFS.011 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-BT02 | =G01NHA01TA001-BT02;XM02 | ELY1 RECT1 TRAFO1 TEMP2 AL2 | 27 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER TEMPERATURE SWITCH - WINDING TEMPERATURE TRIPPING - WINDING TEMPERATURE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BT02 | Temperature switch - Winding temperature | XM02 | Tripping - Winding temperature | Ely1 | Rect1 | Trafo1 | Temp2 | AL2 | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | TIZ | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG12:33 | 33B | 07 | =G01NHA01TA001-BT02&EFS.011 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-BT02 | =G01NHA01TA001-BT02;XM01 | ELY1 RECT1 TRAFO1 TEMP2 AL1 | 27 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER TEMPERATURE SWITCH - WINDING TEMPERATURE WARNING - WINDING TEMPERATURE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BT02 | Temperature switch - Winding temperature | XM01 | Warning - Winding temperature | Ely1 | Rect1 | Trafo1 | Temp2 | AL1 | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | TIZ | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XM01 | EA01 | 04 | =G01NHA01TA001-BT02&EFS.011 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-BU01 | =G01NHA01TA001-BU01;XM02 | ELY1 RECT1 TRAFO1 BUCHH PROT AL2 | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER BUCHHOLZ PROTECTIVE DEVICE - TRANSFORMER TRIPPING - BUCHHOLZ RELAY | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BU01 | Buchholz protective device - Transformer | XM02 | Tripping - Buchholz Relay | Ely1 | Rect1 | Trafo1 | Buchh Prot | AL2 | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | XZ | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG12:15 | 15B | 08 | =G01NHA01TA001-BU01&EFS.007 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-BU01 | =G01NHA01TA001-BU01;XM01 | ELY1 RECT1 TRAFO1 BUCHH PROT AL1 | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER BUCHHOLZ PROTECTIVE DEVICE - TRANSFORMER WARNING - BUCHHOLZ RELAY | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BU01 | Buchholz protective device - Transformer | XM01 | Warning - Buchholz relay | Ely1 | Rect1 | Trafo1 | Buchh Prot | AL1 | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | XZ | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XM01 | EA01 | 05 | =G01NHA01TA001-BU01&EFS.007 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-BU02 | =G01NHA01TA001-BU02;XM01 | ELY1 RECT1 TRAFO1 TAP CHG AL1 | 29 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER PROTECTION RELAY - TAP CHANGER TRIPPING - PROTECTION RELAY - TAP CHANGER | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -BU02 | Protection relay - Tap Changer | XM01 | Tripping - Protection Relay - Tap Changer | Ely1 | Rect1 | Trafo1 | Tap Chg | AL1 | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | XS | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG12:5 | 5B | 09 | =G01NHA01TA001-BU02&EFS.005 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-GP01 | =G01NHA01TA001-GP01;XB13 | ELY1 RECT1 TRAFO1 PMP1 CHECK CMD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER OIL PUMP - TRANSFORMER CHECK COMMAND | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -GP01 | Oil Pump - Transformer | XB13 | Check command | Ely1 | Rect1 | Trafo1 | PMP1 | Check CMD | 1 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | GS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB13 | EA01 | 06 | =G01NHA01TA001-GP01&EFS.008 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-QA01 | =G01NHA01TA001-QA01;XS01 | ELY1 RECT1 TRAFO1 SW1 FB BCD1 | 29 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER TAP CHANGER STEP CONTROL FEEDBACK - BCD 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -QA01 | Tap Changer | XS01 | Step control feedback - BCD 1 | Ely1 | Rect1 | Trafo1 | Sw1 | FB BCD1 | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | GS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XS01 | EA01 | 11 | =G01NHA01TA001-QA01&EFS.004 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-QA01 | =G01NHA01TA001-QA01;XS02 | ELY1 RECT1 TRAFO1 SW1 FB BCD2 | 29 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER TAP CHANGER STEP CONTROL FEEDBACK - BCD 2 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -QA01 | Tap Changer | XS02 | Step control feedback - BCD 2 | Ely1 | Rect1 | Trafo1 | Sw1 | FB BCD2 | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | GS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XS02 | EA01 | 12 | =G01NHA01TA001-QA01&EFS.004 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-QA01 | =G01NHA01TA001-QA01;XS03 | ELY1 RECT1 TRAFO1 SW1 FB BCD3 | 29 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER TAP CHANGER STEP CONTROL FEEDBACK - BCD 4 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -QA01 | Tap Changer | XS03 | Step control feedback - BCD 4 | Ely1 | Rect1 | Trafo1 | Sw1 | FB BCD3 | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | GS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XS03 | EA01 | 13 | =G01NHA01TA001-QA01&EFS.004 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-QA01 | =G01NHA01TA001-QA01;XS04 | ELY1 RECT1 TRAFO1 SW1 FB BCD4 | 29 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER TAP CHANGER STEP CONTROL FEEDBACK - BCD 8 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -QA01 | Tap Changer | XS04 | Step control feedback - BCD 8 | Ely1 | Rect1 | Trafo1 | Sw1 | FB BCD4 | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | GS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XS04 | EA01 | 14 | =G01NHA01TA001-QA01&EFS.004 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-QA01 | =G01NHA01TA001-QA01;XB13 | ELY1 RECT1 TRAFO1 SW1 CHECK CMD | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER TAP CHANGER CHECK COMMAND | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -QA01 | Tap Changer | XB13 | Check command | Ely1 | Rect1 | Trafo1 | Sw1 | Check CMD | 1 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | GS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB13 | EA01 | 07 | =G01NHA01TA001-QA01&EFS.002 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-QA01 | =G01NHA01TA001-QA01;XB14 | ELY1 RECT1 TRAFO1 SW1 CHECK CMD | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER TAP CHANGER CHECK COMMAND | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -QA01 | Tap Changer | XB14 | Check command | Ely1 | Rect1 | Trafo1 | Sw1 | Check CMD | 1 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | GS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB14 | EA01 | 08 | =G01NHA01TA001-QA01&EFS.002 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-QA01 | =G01NHA01TA001-QA01;XR01 | ELY1 RECT1 TRAFO1 SW1 TAP CHG FB H | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER TAP CHANGER MAIN CONTROL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -QA01 | Tap Changer | XR01 | Main control | Ely1 | Rect1 | Trafo1 | Sw1 | TAP CHG FB H | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | GS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XR01 | EA01 | 09 | =G01NHA01TA001-QA01&EFS.003 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-QA01 | =G01NHA01TA001-QA01;XR02 | ELY1 RECT1 TRAFO1 SW1 TAP CHG FB L | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER TAP CHANGER MAIN CONTROL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -QA01 | Tap Changer | XR02 | Main control | Ely1 | Rect1 | Trafo1 | Sw1 | TAP CHG FB L | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | GS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XR02 | EA01 | 10 | =G01NHA01TA001-QA01&EFS.003 |  |  |  | U012UBB01UC001
=G01NHA01TB001 | G01NHA01TB001-GQ01 | =G01NHA01TB001-GQ01;XB13 | ELY1 RECT1 RECT1 RAD BLOW CHECK CMD | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 1 RADIAL BLOWER CHECK COMMAND | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 001 | Rectifier 1 | -GQ01 | Radial blower | XB13 | Check command | Ely1 | Rect1 | Rect1 | Rad Blow | Check CMD |  | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | GS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB13 | EA01 | 06 |  |  |  |  | U012UBB01UC001
=G01NHA01TB001 | G01NHA01TB001-KF01 | =G01NHA01TB001-KF01;XB02 | ELY1 RECT1 RECT1 OUTP MOD CB OFF/CLD | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 1 SINAMICS DCM CONTROL MODULE WITHOUT POWER SECTION CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 001 | Rectifier 1 | -KF01 | SINAMICS DCM CONTROL MODULE WITHOUT POWER SECTION | XB02 | Check back off/closed | Ely1 | Rect1 | Rect1 | Outp Mod | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes | Not defined | =G01NHA01KF001+U012UBB01UC001-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE |  |  | 19 | =G01NHA01TB001-KF01&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01TB002 | G01NHA01TB002-GQ01 | =G01NHA01TB002-GQ01;XB13 | ELY1 RECT1 RECT2 RAD BLOW CHECK CMD | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 2 RADIAL BLOWER CHECK COMMAND | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 002 | Rectifier 2 | -GQ01 | Radial blower | XB13 | Check command | Ely1 | Rect1 | Rect2 | Rad Blow | Check CMD |  | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | GS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB13 | EA01 | 07 |  |  |  |  | U012UBB01UC001
=G01NHA01TB002 | G01NHA01TB002-KF01 | =G01NHA01TB002-KF01;XB02 | ELY1 RECT1 RECT2 OUTP MOD CB OFF/CLD | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 2 SINAMICS DCM CONTROL MODULE WITHOUT POWER SECTION CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 002 | Rectifier 2 | -KF01 | SINAMICS DCM CONTROL MODULE WITHOUT POWER SECTION | XB02 | Check back off/closed | Ely1 | Rect1 | Rect2 | Outp Mod | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes | Not defined | =G01NHA01KF001+U012UBB01UC001-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE |  |  | 20 | =G01NHA01TB002-KF01&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01TB003 | G01NHA01TB003-GQ01 | =G01NHA01TB003-GQ01;XB13 | ELY1 RECT1 RECT3 RAD BLOW CHECK CMD | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 3 RADIAL BLOWER CHECK COMMAND | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 003 | Rectifier 3 | -GQ01 | Radial blower | XB13 | Check command | Ely1 | Rect1 | Rect3 | Rad Blow | Check CMD |  | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | GS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB13 | EA01 | 01 |  |  |  |  | U012UBB01UC002
=G01NHA01TB003 | G01NHA01TB003-KF01 | =G01NHA01TB003-KF01;XB02 | ELY1 RECT1 RECT3 OUTP MOD CB OFF/CLD | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 3 SINAMICS DCM CONTROL MODULE WITHOUT POWER SECTION CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 003 | Rectifier 3 | -KF01 | SINAMICS DCM CONTROL MODULE WITHOUT POWER SECTION | XB02 | Check back off/closed | Ely1 | Rect1 | Rect3 | Outp Mod | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes | Not defined | =G01NHA01KF002+U012UBB01UC002-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | B10:XB02 | XB02A | 05 | =G01NHA01TB003-KF01&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01TB004 | G01NHA01TB004-GQ01 | =G01NHA01TB004-GQ01;XB13 | ELY1 RECT1 RECT4 RAD BLOW CHECK CMD | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 4 RADIAL BLOWER CHECK COMMAND | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 004 | Rectifier 4 | -GQ01 | Radial blower | XB13 | Check command | Ely1 | Rect1 | Rect4 | Rad Blow | Check CMD |  | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | GS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB13 | EA01 | 02 |  |  |  |  | U012UBB01UC002
=G01NHA01TB004 | G01NHA01TB004-KF01 | =G01NHA01TB004-KF01;XB02 | ELY1 RECT1 RECT4 OUTP MOD CB OFF/CLD | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 4 SINAMICS DCM CONTROL MODULE WITHOUT POWER SECTION CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 004 | Rectifier 4 | -KF01 | SINAMICS DCM CONTROL MODULE WITHOUT POWER SECTION | XB02 | Check back off/closed | Ely1 | Rect1 | Rect4 | Outp Mod | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes | Not defined | =G01NHA01KF002+U012UBB01UC002-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | B10:XB02 | XB02A | 17 | =G01NHA01TB004-KF01&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01TB011 | G01NHA01TB011-BA11 | =G01NHA01TB011-BA11;XU01 | ELY1 RECT1 POLR1 400VAC MON GRP FLT | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 1&2 GROUP FAULT ALARM 400VAC GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 011 | Polarisation Rectifier System 1&2 | -BA11 | Group Fault Alarm 400VAC | XU01 | Group fault alarm | Ely1 | Rect1 | Polr1 | 400VAC MON | GRP FLT | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | EAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | XU01B | 16 | =G01NHA01TB011-BA11&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01TB011 | G01NHA01TB011-BA22 | =G01NHA01TB011-BA22;XU01 | ELY1 RECT1 POLR1 230VAC GRP FLT GRP FLT | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 1&2 GROUP FAULT ALARM 230V GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 011 | Polarisation Rectifier System 1&2 | -BA22 | Group Fault Alarm 230V | XU01 | Group fault alarm | Ely1 | Rect1 | Polr1 | 230VAC GRP FLT | GRP FLT | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | EAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC |  |  | 01 | =G01NHA01TB011-BA22&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01TB011 | G01NHA01TB011-BA41 | =G01NHA01TB011-BA41;XU01 | ELY1 RECT1 POLR1 UPS MON GRP FLT | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 1&2 GROUP FAULT ALARM 230V UPS GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 011 | Polarisation Rectifier System 1&2 | -BA41 | Group Fault Alarm 230V UPS | XU01 | Group fault alarm | Ely1 | Rect1 | Polr1 | UPS MON | GRP FLT | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | EAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC |  |  | 02 | =G01NHA01TB011-BA41&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01TB011 | G01NHA01TB011-FC01 | =G01NHA01TB011-FC01;XU01 | ELY1 RECT1 POLR1 24V MON1 GRP FLT | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 1&2 GROUP FAULT ALARM 24VDC UPS DISTRIBUTION GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 011 | Polarisation Rectifier System 1&2 | -FC01 | Group Fault Alarm 24VDC UPS Distribution | XU01 | Group fault alarm | Ely1 | Rect1 | Polr1 | 24V MON1 | GRP FLT | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC |  |  | 03 | =G01NHA01TB011-FC01&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01TB011 | G01NHA01TB011-KF11 | =G01NHA01TB011-KF11;XB02 | ELY1 RECT1 POLR1 DCM1 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 1&2 SINAMICS DCM - STO CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 011 | Polarisation Rectifier System 1&2 | -KF11 | SINAMICS DCM - STO | XB02 | Check back off/closed | Ely1 | Rect1 | Polr1 | DCM1 | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes | Not defined | =G01NHA01KF001+U012UBB01UC001-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG03:3 | 3B | 10 | =G01NHA01TB011-KF11&EFS.002 |  |  |  | U012UBB01UC001
=G01NHA01TB011 | G01NHA01TB011-KF12 | =G01NHA01TB011-KF12;XB02 | ELY1 RECT1 POLR1 DCM2 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 1&2 SINAMICS DCM - STO CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 011 | Polarisation Rectifier System 1&2 | -KF12 | SINAMICS DCM - STO | XB02 | Check back off/closed | Ely1 | Rect1 | Polr1 | DCM2 | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes | Not defined | =G01NHA01KF001+U012UBB01UC001-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG03:11 | 11B | 22 | =G01NHA01TB011-KF12&EFS.002 |  |  |  | U012UBB01UC001
=G01NHA01TB011 | G01NHA01TB011-QA03 | =G01NHA01TB011-QA03;XB02 | ELY1 RECT1 POLR1 SW3 CB OFF/CLD | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 1&2 MAINSWITCH - OFF CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 011 | Polarisation Rectifier System 1&2 | -QA03 | Mainswitch - OFF | XB02 | Check back off/closed | Ely1 | Rect1 | Polr1 | Sw3 | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes | Not defined | =G01NHA01KF001+U012UBB01UC001-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG03:7 | 7B | 11 | =G01NHA01TB011-QA03&EFS.002 |  |  |  | U012UBB01UC001
=G01NHA01TB011 | G01NHA01TB011-QA04 | =G01NHA01TB011-QA04;XB02 | ELY1 RECT1 POLR1 SW4 CB OFF/CLD | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 1&2 MAINSWITCH - OFF CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 011 | Polarisation Rectifier System 1&2 | -QA04 | Mainswitch - OFF | XB02 | Check back off/closed | Ely1 | Rect1 | Polr1 | Sw4 | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes | Not defined | =G01NHA01KF001+U012UBB01UC001-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG03:15 | 15B | 23 | =G01NHA01TB011-QA04&EFS.002 |  |  |  | U012UBB01UC001
=G01NHA01TB011 | G01NHA01TB011-QB03 | =G01NHA01TB011-QB03;XB02 | ELY1 RECT1 POLR1 DISC SYS1 CB OFF/CLD | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 1&2 DC DISCONNECT SWITCH - SYSTEM 1 CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 011 | Polarisation Rectifier System 1&2 | -QB03 | DC disconnect switch - System 1 | XB02 | Check back off/closed | Ely1 | Rect1 | Polr1 | Disc Sys1 | CB OFF/CLD | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GS | [13 empty] | Yes | Not defined | =G01NHA01KF001+U012UBB01UC001-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC |  |  | 11 | =G01NHA01TB011-QB03&EFS.002 |  |  |  | U012UBB01UC001
=G01NHA01TB011 | G01NHA01TB011-QB04 | =G01NHA01TB011-QB04;XB02 | ELY1 RECT1 POLR1 DISC SYS2 CB OFF/CLD | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 1&2 DC DISCONNECT SWITCH - SYSTEM 2 CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 011 | Polarisation Rectifier System 1&2 | -QB04 | DC disconnect switch - System 2 | XB02 | Check back off/closed | Ely1 | Rect1 | Polr1 | Disc Sys2 | CB OFF/CLD | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GS | [13 empty] | Yes | Not defined | =G01NHA01KF001+U012UBB01UC001-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB02 | XB02B | 12 | =G01NHA01TB011-QB04&EFS.002 |  |  |  | U012UBB01UC001
=G01NHA01TB011 | G01NHA01TB011-TB01 | =G01NHA01TB011-TB01;XU01 | ELY1 RECT1 POLR1 24VDC MON1 GRP FLT | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 1&2 GROUP FAULT ALARM 24VDC UPS GENERATION GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 011 | Polarisation Rectifier System 1&2 | -TB01 | Group Fault Alarm 24VDC UPS Generation | XU01 | Group fault alarm | Ely1 | Rect1 | Polr1 | 24VDC MON1 | GRP FLT | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC |  |  | 15 | =G01NHA01TB011-TB01&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01TB012 | G01NHA01TB012-BA11 | =G01NHA01TB012-BA11;XU01 | ELY1 RECT1 POLR2 400VAC MON GRP FLT | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 3&4 GROUP FAULT ALARM 400VAC GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 012 | Polarisation Rectifier System 3&4 | -BA11 | Group Fault Alarm 400VAC | XU01 | Group fault alarm | Ely1 | Rect1 | Polr2 | 400VAC MON | GRP FLT | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | EAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | XU01B | 12 | =G01NHA01TB012-BA11&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01TB012 | G01NHA01TB012-BA22 | =G01NHA01TB012-BA22;XU01 | ELY1 RECT1 POLR2 230VAC GRP FLT GRP FLT | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 3&4 GROUP FAULT ALARM 230V GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 012 | Polarisation Rectifier System 3&4 | -BA22 | Group Fault Alarm 230V | XU01 | Group fault alarm | Ely1 | Rect1 | Polr2 | 230VAC GRP FLT | GRP FLT | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | EAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | XU01B | 13 | =G01NHA01TB012-BA22&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01TB012 | G01NHA01TB012-BA41 | =G01NHA01TB012-BA41;XU01 | ELY1 RECT1 POLR2 UPS MON GRP FLT | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 3&4 GROUP FAULT ALARM 230V UPS GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 012 | Polarisation Rectifier System 3&4 | -BA41 | Group Fault Alarm 230V UPS | XU01 | Group fault alarm | Ely1 | Rect1 | Polr2 | UPS MON | GRP FLT | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | EAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | XU01B | 14 | =G01NHA01TB012-BA41&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01TB012 | G01NHA01TB012-FC01 | =G01NHA01TB012-FC01;XU01 | ELY1 RECT1 POLR2 24V MON1 GRP FLT | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 3&4 GROUP FAULT ALARM 24VDC UPS DISTRIBUTION GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 012 | Polarisation Rectifier System 3&4 | -FC01 | Group Fault Alarm 24VDC UPS Distribution | XU01 | Group fault alarm | Ely1 | Rect1 | Polr2 | 24V MON1 | GRP FLT | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | XU01A | 15 | =G01NHA01TB012-FC01&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01TB012 | G01NHA01TB012-KF11 | =G01NHA01TB012-KF11;XB02 | ELY1 RECT1 POLR2 DCM1 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 3&4 SINAMICS DCM - STO CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 012 | Polarisation Rectifier System 3&4 | -KF11 | SINAMICS DCM - STO | XB02 | Check back off/closed | Ely1 | Rect1 | Polr2 | DCM1 | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes | Not defined | =G01NHA01KF002+U012UBB01UC002-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG03:3 | 3B | 10 | =G01NHA01TB012-KF11&EFS.002 |  |  |  | U012UBB01UC002
=G01NHA01TB012 | G01NHA01TB012-KF12 | =G01NHA01TB012-KF12;XB02 | ELY1 RECT1 POLR2 DCM2 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 3&4 SINAMICS DCM - STO CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 012 | Polarisation Rectifier System 3&4 | -KF12 | SINAMICS DCM - STO | XB02 | Check back off/closed | Ely1 | Rect1 | Polr2 | DCM2 | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes | Not defined | =G01NHA01KF002+U012UBB01UC002-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG03:11 | 11B | 22 | =G01NHA01TB012-KF12&EFS.002 |  |  |  | U012UBB01UC002
=G01NHA01TB012 | G01NHA01TB012-QA03 | =G01NHA01TB012-QA03;XB02 | ELY1 RECT1 POLR2 SW3 CB OFF/CLD | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 3&4 MAINSWITCH - OFF CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 012 | Polarisation Rectifier System 3&4 | -QA03 | Mainswitch - OFF | XB02 | Check back off/closed | Ely1 | Rect1 | Polr2 | Sw3 | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes | Not defined | =G01NHA01KF002+U012UBB01UC002-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG03:7 | 7B | 11 | =G01NHA01TB012-QA03&EFS.002 |  |  |  | U012UBB01UC002
=G01NHA01TB012 | G01NHA01TB012-QA04 | =G01NHA01TB012-QA04;XB02 | ELY1 RECT1 POLR2 SW4 CB OFF/CLD | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 3&4 MAINSWITCH - OFF CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 012 | Polarisation Rectifier System 3&4 | -QA04 | Mainswitch - OFF | XB02 | Check back off/closed | Ely1 | Rect1 | Polr2 | Sw4 | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GS | [13 empty] | Yes | Not defined | =G01NHA01KF002+U012UBB01UC002-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG03:15 | 15B | 23 | =G01NHA01TB012-QA04&EFS.002 |  |  |  | U012UBB01UC002
=G01NHA01TB012 | G01NHA01TB012-QB03 | =G01NHA01TB012-QB03;XB02 | ELY1 RECT1 POLR2 DISC SYS1 CB OFF/CLD | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 3&4 DC DISCONNECT SWITCH - SYSTEM 1 CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 012 | Polarisation Rectifier System 3&4 | -QB03 | DC disconnect switch - System 1 | XB02 | Check back off/closed | Ely1 | Rect1 | Polr2 | Disc Sys1 | CB OFF/CLD | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GS | [13 empty] | Yes | Not defined | =G01NHA01KF002+U012UBB01UC002-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB02 | XB02B | 03 | =G01NHA01TB012-QB03&EFS.002 |  |  |  | U012UBB01UC002
=G01NHA01TB012 | G01NHA01TB012-QB04 | =G01NHA01TB012-QB04;XB02 | ELY1 RECT1 POLR2 DISC SYS2 CB OFF/CLD | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 3&4 DC DISCONNECT SWITCH - SYSTEM 2 CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 012 | Polarisation Rectifier System 3&4 | -QB04 | DC disconnect switch - System 2 | XB02 | Check back off/closed | Ely1 | Rect1 | Polr2 | Disc Sys2 | CB OFF/CLD | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GS | [13 empty] | Yes | Not defined | =G01NHA01KF002+U012UBB01UC002-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB02 | XB02B | 04 | =G01NHA01TB012-QB04&EFS.002 |  |  |  | U012UBB01UC002
=G01NHA01TB012 | G01NHA01TB012-TB01 | =G01NHA01TB012-TB01;XU01 | ELY1 RECT1 POLR2 24VDC MON1 GRP FLT | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 3&4 GROUP FAULT ALARM 24VDC UPS GENERATION GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 012 | Polarisation Rectifier System 3&4 | -TB01 | Group Fault Alarm 24VDC UPS Generation | XU01 | Group fault alarm | Ely1 | Rect1 | Polr2 | 24VDC MON1 | GRP FLT | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | XU01B | 16 | =G01NHA01TB012-TB01&EFS.001 |  |  |  | U012UBB01UC002
=G01NHB01EQ001 | G01NHB01EQ001-QN01 | =G01NHB01EQ001-QN01;XU01 | ELY1 GRP1 COOL CV1 GRP FLT | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 COOLING WATER - CONTROL VALVE GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -QN01 | Cooling Water - Control Valve | XU01 | Group fault alarm | Ely1 | Grp1 | Cool | CV1 | GRP FLT | -QN01KF01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | YC | [15 empty] | =G01NHB01KF002+U012UNA01UH111-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART |  |  | 16 | =G01NHB01EQ001-QN01&EFS.001 | =G01NHB01&MFB.001 |  |  | U012UNA01UH111
=G01NHB01KF001 | G01NHB01KF001-FC02 | =G01NHB01KF001-FC02;XW01 | ELY1 GRP1 CTRL U1 24V MON2 AL/FLT CODE | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 CONTROL UNITS CELL VOLTAGE MEASUREMENT SITOP SEL1200 SELECTIVITY MODULE 8-CHANNEL VOLTAGE SUPPLY FAIL 8X 24VDC | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | KF | Control Units | 001 | Cell Voltage Measurement | -FC02 | SITOP SEL1200 Selectivity module 8-channel | XW01 | Voltage supply fail 8x 24VDC | Ely1 | Grp1 | CTRL U1 | 24V MON2 | AL/FLT CODE | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 02 | =G01NHB01KF001-FC02&EFS.004 |  |  |  | U012UNA01UH100
=G01NHB01KF001 | G01NHB01KF001-TB01 | =G01NHB01KF001-TB01;XW01 | ELY1 GRP1 CTRL U1 24VDC MON1 AL/FLT CODE | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 CONTROL UNITS CELL VOLTAGE MEASUREMENT SITOP PSU6200 24 V/20 A VOLTAGE SUPPLY FAIL 230/24V DC | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | KF | Control Units | 001 | Cell Voltage Measurement | -TB01 | SITOP PSU6200 24 V/20 A | XW01 | Voltage supply fail 230/24V DC | Ely1 | Grp1 | CTRL U1 | 24VDC MON1 | AL/FLT CODE | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Continuous signal |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 03 | =G01NHB01KF001-TB01&EFS.004 |  |  |  | U012UNA01UH100
=G01NHB01KF002 | G01NHB01KF002-FC01 | =G01NHB01KF002-FC01;XW01 | ELY1 GRP1 CTRL U2 24V MON1 AL/FLT CODE | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 CONTROL UNITS MODULE GROUP CONTROL UNIT SITOP SEL1200 SELECTIVITY MODULE 8-CHANNEL VOLTAGE SUPPLY FAIL 8X 24VDC | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | KF | Control Units | 002 | Module Group Control Unit | -FC01 | SITOP SEL1200 Selectivity module 8-channel | XW01 | Voltage supply fail 8x 24VDC | Ely1 | Grp1 | CTRL U2 | 24V MON1 | AL/FLT CODE | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 01 | =G01NHB01KF002-FC01&EFS.003 |  |  |  | U012UNA01UH100
=G01NHB02EQ001 | G01NHB02EQ001-QN01 | =G01NHB02EQ001-QN01;XU01 | ELY1 GRP2 COOL CV1 GRP FLT | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 COOLING WATER - CONTROL VALVE GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -QN01 | Cooling Water - Control Valve | XU01 | Group fault alarm | Ely1 | Grp2 | Cool | CV1 | GRP FLT | -QN01KF01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | YC | [15 empty] | =G01NHB02KF002+U012UNA01UH121-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XU01 | EA01 | 16 | =G01NHB02EQ001-QN01&EFS.001 | =G01NHB02&MFB.001 |  |  | U012UNA01UH121
=G01NHB02KF001 | G01NHB02KF001-FC02 | =G01NHB02KF001-FC02;XW01 | ELY1 GRP2 CTRL U1 24V MON2 AL/FLT CODE | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 CONTROL UNITS CELL VOLTAGE MEASUREMENT SITOP SEL1200 SELECTIVITY MODULE 8-CHANNEL VOLTAGE SUPPLY FAIL 8X 24VDC | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | KF | Control Units | 001 | Cell Voltage Measurement | -FC02 | SITOP SEL1200 Selectivity module 8-channel | XW01 | Voltage supply fail 8x 24VDC | Ely1 | Grp2 | CTRL U1 | 24V MON2 | AL/FLT CODE | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 05 | =G01NHB02KF001-FC02&EFS.004 |  |  |  | U012UNA01UH100
=G01NHB02KF001 | G01NHB02KF001-TB01 | =G01NHB02KF001-TB01;XW01 | ELY1 GRP2 CTRL U1 24VDC MON1 AL/FLT CODE | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 CONTROL UNITS CELL VOLTAGE MEASUREMENT SITOP PSU6200 24 V/20 A VOLTAGE SUPPLY FAIL 230/24V DC | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | KF | Control Units | 001 | Cell Voltage Measurement | -TB01 | SITOP PSU6200 24 V/20 A | XW01 | Voltage supply fail 230/24V DC | Ely1 | Grp2 | CTRL U1 | 24VDC MON1 | AL/FLT CODE | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Continuous signal |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 06 | =G01NHB02KF001-TB01&EFS.004 |  |  |  | U012UNA01UH100
=G01NHB02KF002 | G01NHB02KF002-FC01 | =G01NHB02KF002-FC01;XW01 | ELY1 GRP2 CTRL U2 24V MON1 AL/FLT CODE | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 CONTROL UNITS MODULE GROUP CONTROL UNIT SITOP SEL1200 SELECTIVITY MODULE 8-CHANNEL VOLTAGE SUPPLY FAIL 8X 24VDC | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | KF | Control Units | 002 | Module Group Control Unit | -FC01 | SITOP SEL1200 Selectivity module 8-channel | XW01 | Voltage supply fail 8x 24VDC | Ely1 | Grp2 | CTRL U2 | 24V MON1 | AL/FLT CODE | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 04 | =G01NHB02KF002-FC01&EFS.003 |  |  |  | U012UNA01UH100
=G01NHB03EQ001 | G01NHB03EQ001-QN01 | =G01NHB03EQ001-QN01;XU01 | ELY1 GRP3 COOL CV1 GRP FLT | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 COOLING WATER - CONTROL VALVE GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -QN01 | Cooling Water - Control Valve | XU01 | Group fault alarm | Ely1 | Grp3 | Cool | CV1 | GRP FLT | -QN01KF01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | YC | [15 empty] | =G01NHB03KF002+U012UNA01UH131-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XU01 | EA01 | 16 | =G01NHB03EQ001-QN01&EFS.001 | =G01NHB03&MFB.001 |  |  | U012UNA01UH131
=G01NHB03KF001 | G01NHB03KF001-FC02 | =G01NHB03KF001-FC02;XW01 | ELY1 GRP3 CTRL U1 24V MON2 AL/FLT CODE | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 CONTROL UNITS CELL VOLTAGE MEASUREMENT SITOP SEL1200 SELECTIVITY MODULE 8-CHANNEL VOLTAGE SUPPLY FAIL 8X 24VDC | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | KF | Control Units | 001 | Cell Voltage Measurement | -FC02 | SITOP SEL1200 Selectivity module 8-channel | XW01 | Voltage supply fail 8x 24VDC | Ely1 | Grp3 | CTRL U1 | 24V MON2 | AL/FLT CODE | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 08 | =G01NHB03KF001-FC02&EFS.004 |  |  |  | U012UNA01UH100
=G01NHB03KF001 | G01NHB03KF001-TB01 | =G01NHB03KF001-TB01;XW01 | ELY1 GRP3 CTRL U1 24VDC MON1 AL/FLT CODE | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 CONTROL UNITS CELL VOLTAGE MEASUREMENT SITOP PSU6200 24 V/20 A VOLTAGE SUPPLY FAIL 230/24V DC | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | KF | Control Units | 001 | Cell Voltage Measurement | -TB01 | SITOP PSU6200 24 V/20 A | XW01 | Voltage supply fail 230/24V DC | Ely1 | Grp3 | CTRL U1 | 24VDC MON1 | AL/FLT CODE | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Continuous signal |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 09 | =G01NHB03KF001-TB01&EFS.004 |  |  |  | U012UNA01UH100
=G01NHB03KF002 | G01NHB03KF002-FC01 | =G01NHB03KF002-FC01;XW01 | ELY1 GRP3 CTRL U2 24V MON1 AL/FLT CODE | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 CONTROL UNITS MODULE GROUP CONTROL UNIT SITOP SEL1200 SELECTIVITY MODULE 8-CHANNEL VOLTAGE SUPPLY FAIL 8X 24VDC | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | KF | Control Units | 002 | Module Group Control Unit | -FC01 | SITOP SEL1200 Selectivity module 8-channel | XW01 | Voltage supply fail 8x 24VDC | Ely1 | Grp3 | CTRL U2 | 24V MON1 | AL/FLT CODE | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 07 | =G01NHB03KF002-FC01&EFS.003 |  |  |  | U012UNA01UH100
=G01NHB04EQ001 | G01NHB04EQ001-QN01 | =G01NHB04EQ001-QN01;XU01 | ELY1 GRP4 COOL CV1 GRP FLT | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 COOLING WATER - CONTROL VALVE GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -QN01 | Cooling Water - Control Valve | XU01 | Group fault alarm | Ely1 | Grp4 | Cool | CV1 | GRP FLT | -QN01KF01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | YC | [15 empty] | =G01NHB04KF002+U012UNA01UH141-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XU01 | EA01 | 16 | =G01NHB04EQ001-QN01&EFS.001 | =G01NHB04&MFB.001 |  |  | U012UNA01UH141
=G01NHB04KF001 | G01NHB04KF001-FC02 | =G01NHB04KF001-FC02;XW01 | ELY1 GRP4 CTRL U1 24V MON2 AL/FLT CODE | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 CONTROL UNITS CELL VOLTAGE MEASUREMENT SITOP SEL1200 SELECTIVITY MODULE 8-CHANNEL VOLTAGE SUPPLY FAIL 8X 24VDC | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | KF | Control Units | 001 | Cell Voltage Measurement | -FC02 | SITOP SEL1200 Selectivity module 8-channel | XW01 | Voltage supply fail 8x 24VDC | Ely1 | Grp4 | CTRL U1 | 24V MON2 | AL/FLT CODE | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 11 | =G01NHB04KF001-FC02&EFS.004 |  |  |  | U012UNA01UH100
=G01NHB04KF001 | G01NHB04KF001-TB01 | =G01NHB04KF001-TB01;XW01 | ELY1 GRP4 CTRL U1 24VDC MON1 AL/FLT CODE | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 CONTROL UNITS CELL VOLTAGE MEASUREMENT SITOP PSU6200 24 V/20 A VOLTAGE SUPPLY FAIL 230/24V DC | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | KF | Control Units | 001 | Cell Voltage Measurement | -TB01 | SITOP PSU6200 24 V/20 A | XW01 | Voltage supply fail 230/24V DC | Ely1 | Grp4 | CTRL U1 | 24VDC MON1 | AL/FLT CODE | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Continuous signal |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 12 | =G01NHB04KF001-TB01&EFS.004 |  |  |  | U012UNA01UH100
=G01NHB04KF002 | G01NHB04KF002-FC01 | =G01NHB04KF002-FC01;XW01 | ELY1 GRP4 CTRL U2 24V MON1 AL/FLT CODE | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 CONTROL UNITS MODULE GROUP CONTROL UNIT SITOP SEL1200 SELECTIVITY MODULE 8-CHANNEL VOLTAGE SUPPLY FAIL 8X 24VDC | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | KF | Control Units | 002 | Module Group Control Unit | -FC01 | SITOP SEL1200 Selectivity module 8-channel | XW01 | Voltage supply fail 8x 24VDC | Ely1 | Grp4 | CTRL U2 | 24V MON1 | AL/FLT CODE | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 10 | =G01NHB04KF002-FC01&EFS.003 |  |  |  | U012UNA01UH100
=G01NHB05EQ001 | G01NHB05EQ001-QN01 | =G01NHB05EQ001-QN01;XU01 | ELY1 GRP5 COOL CV1 GRP FLT | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 COOLING WATER - CONTROL VALVE GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -QN01 | Cooling Water - Control Valve | XU01 | Group fault alarm | Ely1 | Grp5 | Cool | CV1 | GRP FLT | -QN01KF01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | YC | [15 empty] | =G01NHB05KF002+U012UNA01UH151-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XU01 | EA01 | 16 | =G01NHB05EQ001-QN01&EFS.001 | =G01NHB05&MFB.001 |  |  | U012UNA01UH151
=G01NHB05KF001 | G01NHB05KF001-FC02 | =G01NHB05KF001-FC02;XW01 | ELY1 GRP5 CTRL U1 24V MON2 AL/FLT CODE | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 CONTROL UNITS CELL VOLTAGE MEASUREMENT SITOP SEL1200 SELECTIVITY MODULE 8-CHANNEL VOLTAGE SUPPLY FAIL 8X 24VDC | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | KF | Control Units | 001 | Cell Voltage Measurement | -FC02 | SITOP SEL1200 Selectivity module 8-channel | XW01 | Voltage supply fail 8x 24VDC | Ely1 | Grp5 | CTRL U1 | 24V MON2 | AL/FLT CODE | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 14 | =G01NHB05KF001-FC02&EFS.004 |  |  |  | U012UNA01UH100
=G01NHB05KF001 | G01NHB05KF001-TB01 | =G01NHB05KF001-TB01;XW01 | ELY1 GRP5 CTRL U1 24VDC MON1 AL/FLT CODE | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 CONTROL UNITS CELL VOLTAGE MEASUREMENT SITOP PSU6200 24 V/20 A VOLTAGE SUPPLY FAIL 230/24V DC | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | KF | Control Units | 001 | Cell Voltage Measurement | -TB01 | SITOP PSU6200 24 V/20 A | XW01 | Voltage supply fail 230/24V DC | Ely1 | Grp5 | CTRL U1 | 24VDC MON1 | AL/FLT CODE | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Continuous signal |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 15 | =G01NHB05KF001-TB01&EFS.004 |  |  |  | U012UNA01UH100
=G01NHB05KF002 | G01NHB05KF002-FC01 | =G01NHB05KF002-FC01;XW01 | ELY1 GRP5 CTRL U2 24V MON1 AL/FLT CODE | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 CONTROL UNITS MODULE GROUP CONTROL UNIT SITOP SEL1200 SELECTIVITY MODULE 8-CHANNEL VOLTAGE SUPPLY FAIL 8X 24VDC | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | KF | Control Units | 002 | Module Group Control Unit | -FC01 | SITOP SEL1200 Selectivity module 8-channel | XW01 | Voltage supply fail 8x 24VDC | Ely1 | Grp5 | CTRL U2 | 24V MON1 | AL/FLT CODE | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 13 | =G01NHB05KF002-FC01&EFS.003 |  |  |  | U012UNA01UH100
=G01NHB06EQ001 | G01NHB06EQ001-QN01 | =G01NHB06EQ001-QN01;XU01 | ELY1 GRP6 COOL CV1 GRP FLT | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 HEAT EXCHANGING SYSTEMS HEAT EXCHANGING SYSTEM 1 COOLING WATER - CONTROL VALVE GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | EQ | Heat Exchanging Systems | 001 | Heat Exchanging System 1 | -QN01 | Cooling Water - Control Valve | XU01 | Group fault alarm | Ely1 | Grp6 | Cool | CV1 | GRP FLT | -QN01KF01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | YC | [15 empty] | =G01NHB06KF002+U012UNA01UH161-KF02 | 6DL1 133-6EW00-0EH1, ET 200SP HA, AI-DI16/DQ16X24VDC HART | B10:XU01 | EA01 | 16 | =G01NHB06EQ001-QN01&EFS.001 | =G01NHB06&MFB.001 |  |  | U012UNA01UH161
=G01NHB06KF001 | G01NHB06KF001-FC02 | =G01NHB06KF001-FC02;XW01 | ELY1 GRP6 CTRL U1 24V MON2 AL/FLT CODE | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 CONTROL UNITS CELL VOLTAGE MEASUREMENT SITOP SEL1200 SELECTIVITY MODULE 8-CHANNEL VOLTAGE SUPPLY FAIL 8X 24VDC | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | KF | Control Units | 001 | Cell Voltage Measurement | -FC02 | SITOP SEL1200 Selectivity module 8-channel | XW01 | Voltage supply fail 8x 24VDC | Ely1 | Grp6 | CTRL U1 | 24V MON2 | AL/FLT CODE | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 01 | =G01NHB06KF001-FC02&EFS.004 |  |  |  | U012UNA01UH100
=G01NHB06KF001 | G01NHB06KF001-TB01 | =G01NHB06KF001-TB01;XW01 | ELY1 GRP6 CTRL U1 24VDC MON1 AL/FLT CODE | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 CONTROL UNITS CELL VOLTAGE MEASUREMENT SITOP PSU6200 24 V/20 A VOLTAGE SUPPLY FAIL 230/24V DC | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | KF | Control Units | 001 | Cell Voltage Measurement | -TB01 | SITOP PSU6200 24 V/20 A | XW01 | Voltage supply fail 230/24V DC | Ely1 | Grp6 | CTRL U1 | 24VDC MON1 | AL/FLT CODE | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Continuous signal |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 02 | =G01NHB06KF001-TB01&EFS.004 |  |  |  | U012UNA01UH100
=G01NHB06KF002 | G01NHB06KF002-FC01 | =G01NHB06KF002-FC01;XW01 | ELY1 GRP6 CTRL U2 24V MON1 AL/FLT CODE | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 CONTROL UNITS MODULE GROUP CONTROL UNIT SITOP SEL1200 SELECTIVITY MODULE 8-CHANNEL VOLTAGE SUPPLY FAIL 8X 24VDC | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | KF | Control Units | 002 | Module Group Control Unit | -FC01 | SITOP SEL1200 Selectivity module 8-channel | XW01 | Voltage supply fail 8x 24VDC | Ely1 | Grp6 | CTRL U2 | 24V MON1 | AL/FLT CODE | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XW01 | EA01 | 16 | =G01NHB06KF002-FC01&EFS.003 |  |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-BP10 | =G01NHC01BQ001-BP10;XG01 | ELY1 H2 TRT QUAL PRES SW CB ON/OPN/MAX1 | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM PRESSURE SWITCH CHECK BACK ON/OPEN // LIMIT VALUE >MAX 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -BP10 | Pressure switch | XG01 | Check back on/open // Limit value >max 1 | Ely1 | H2 TRT | QUAL | Pres sw | CB ON/OPN/MAX1 | -BP10 | Electrical | 24 VAC | 24 VAC | Wire | Normally closed |  |  | DI | 0 | PIS | [9 empty] | AL | [5 empty] | =G01NHY01KF001+U012UNA01UH100-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XG01 | EA01 | 07 | =G01NHC01BQ001-BP10&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-BQ01 | =G01NHC01BQ001-BQ01;XM01 | ELY1 H2 TRT QUAL QUAL1 AL1 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM 11012; O2-MEASURING SENSOR FAULT | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -BQ01 | 11012; O2-measuring sensor | XM01 | Fault | Ely1 | H2 TRT | QUAL | Qual1 | AL1 | -BQ01 | Electrical | 24 VAC | 24 VAC | Wire | Normally closed |  |  | _ | 0 | XS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XM01 | EA01 | 09 | =G01NHC01BQ001-BQ01&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-BQ01 | =G01NHC01BQ001-BQ01;XQ01 | ELY1 H2 TRT QUAL QUAL1 ANALOG1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM 11012; O2-MEASURING SENSOR ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -BQ01 | 11012; O2-measuring sensor | XQ01 | Analog process signal | Ely1 | H2 TRT | QUAL | Qual1 | ANALOG1 | -BQ01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | AI | [5 empty] | ASHH |  | AH | [5 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF06 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | XG06:4 | 4d | 02 | =G01NHC01BQ001-BQ01&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-BQ01 | =G01NHC01BQ001-BQ01;XJ01 | ELY1 H2 TRT QUAL QUAL1 RDY F OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM 11012; O2-MEASURING SENSOR FUNCTIONAL CHECK | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -BQ01 | 11012; O2-measuring sensor | XJ01 | Functional check | Ely1 | H2 TRT | QUAL | Qual1 | RDY F OP | -BQ01 | Electrical | 24 VAC | 24 VAC | Wire | Normally closed |  |  | DI | 0 | XS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XJ01 | EA01 | 08 | =G01NHC01BQ001-BQ01&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-BQ02 | =G01NHC01BQ001-BQ02;XQ01 | ELY1 H2 TRT QUAL QUAL2 ANALOG1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM 11012; O2-MEASURING SENSOR ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -BQ02 | 11012; O2-measuring sensor | XQ01 | Analog process signal | Ely1 | H2 TRT | QUAL | Qual2 | ANALOG1 | -BQ02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | AI | [5 empty] | ASHH |  | AH | [5 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF06 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | XG06:6 | 6d | 03 | =G01NHC01BQ001-BQ02&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-BQ02 | =G01NHC01BQ001-BQ02;XM01 | ELY1 H2 TRT QUAL QUAL2 AL1 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM 11012; O2-MEASURING SENSOR FAULT | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -BQ02 | 11012; O2-measuring sensor | XM01 | Fault | Ely1 | H2 TRT | QUAL | Qual2 | AL1 | -BQ02 | Electrical | 24 VAC | 24 VAC | Wire | Normally closed |  |  | DI | 0 | XS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XM01 | EA01 | 11 | =G01NHC01BQ001-BQ02&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-BQ02 | =G01NHC01BQ001-BQ02;XJ01 | ELY1 H2 TRT QUAL QUAL2 RDY F OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM 11012; O2-MEASURING SENSOR FUNCTIONAL CHECK | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -BQ02 | 11012; O2-measuring sensor | XJ01 | Functional check | Ely1 | H2 TRT | QUAL | Qual2 | RDY F OP | -BQ02 | Electrical | 24 VAC | 24 VAC | Wire | Normally closed |  |  | DI | 0 | XS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XJ01 | EA01 | 10 | =G01NHC01BQ001-BQ02&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-EQ01 | =G01NHC01BQ001-EQ01;XU01 | ELY1 H2 TRT QUAL GAS COOL GRP FLT | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM GAS COOLER H2 GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -EQ01 | Gas Cooler H2 | XU01 | Group fault alarm | Ely1 | H2 TRT | QUAL | Gas Cool | GRP FLT | X?? | Electrical | 24 VAC | 24 VAC | Wire | Normally closed |  |  | DI | 0 | XS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | EA01 | 13 | =G01NHC01BQ001-EQ01&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-EQ01 | =G01NHC01BQ001-EQ01;XB13 | ELY1 H2 TRT QUAL GAS COOL CHECK CMD | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM GAS COOLER H2 CHECK COMMAND | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -EQ01 | Gas Cooler H2 | XB13 | Check command | Ely1 | H2 TRT | QUAL | Gas Cool | Check CMD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | NS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10_1:XB13 | EA01 | 12 | =G01NHC01BQ001-EQ01&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-EQ01 | =G01NHC01BQ001-EQ01;YB11 | ELY1 H2 TRT QUAL GAS COOL CMD ON/OP | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM GAS COOLER H2 MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -EQ01 | Gas Cooler H2 | YB11 | Manual command ON/OPEN | Ely1 | H2 TRT | QUAL | Gas Cool | CMD ON/OP | -XG01 | Electrical | 24 VAC | 24 VAC | Wire | Normally closed |  |  | DO | 0 | NS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF09 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10_1:YB11 | EA01 | 02 | =G01NHC01BQ001-EQ01&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-FC01 | =G01NHC01BQ001-FC01;XU01 | ELY1 H2 TRT QUAL 24V MON1 GRP FLT | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM GENERAL FEEDBACK - POWER SUPPLY GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -FC01 | General Feedback - Power Supply | XU01 | Group fault alarm | Ely1 | H2 TRT | QUAL | 24V MON1 | GRP FLT | -XG01 | Electrical | 24 VAC | 24 VAC | Wire | Normally closed |  |  | DI | 0 | XS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | EA01 | 14 | =G01NHC01BQ001-FC01&EFS.002 |  |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-GP01 | =G01NHC01BQ001-GP01;XB13 | ELY1 H2 TRT QUAL PMP1 CHECK CMD | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM GAS ANALYTIC PUMP, H2 CHECK COMMAND | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -GP01 | Gas Analytic Pump, H2 | XB13 | Check command | Ely1 | H2 TRT | QUAL | PMP1 | Check CMD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | NS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10_1:XB13 | EA01 | 15 | =G01NHC01BQ001-GP01&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-GP01 | =G01NHC01BQ001-GP01;YB11 | ELY1 H2 TRT QUAL PMP1 CMD ON/OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM GAS ANALYTIC PUMP, H2 MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -GP01 | Gas Analytic Pump, H2 | YB11 | Manual command ON/OPEN | Ely1 | H2 TRT | QUAL | PMP1 | CMD ON/OP | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 0 | NS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF09 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10_1:YB11 | EA01 | 01 | =G01NHC01BQ001-GP01&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM11 | =G01NHC01BQ001-QM11;XB01 | ELY1 H2 TRT QUAL SV11 CB ON/OPN | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM11 | Solenoid valve | XB01 | Check back on/open | Ely1 | H2 TRT | QUAL | SV11 | CB ON/OPN | -QM11BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:27 | 27B | 02 | =G01NHC01BQ001-QM11&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM11 | =G01NHC01BQ001-QM11;XB02 | ELY1 H2 TRT QUAL SV11 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM11 | Solenoid valve | XB02 | Check back off/closed | Ely1 | H2 TRT | QUAL | SV11 | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:17 | 17d | 14 | =G01NHC01BQ001-QM11&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM11 | =G01NHC01BQ001-QM11;YB11 | ELY1 H2 TRT QUAL SV11 CMD ON/OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM11 | Solenoid valve | YB11 | Manual command ON/OPEN | Ely1 | H2 TRT | QUAL | SV11 | CMD ON/OP | -QM11MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DO | 0 | YS | [14 empty] | Not defined | =G01NHY01KF001+U012UNA01UH100-KF09 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 03 | =G01NHC01BQ001-QM11&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM12 | =G01NHC01BQ001-QM12;XB01 | ELY1 H2 TRT QUAL SV12 CB ON/OPN | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM12 | Solenoid valve | XB01 | Check back on/open | Ely1 | H2 TRT | QUAL | SV12 | CB ON/OPN | -QM12BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:32 | 32B | 03 | =G01NHC01BQ001-QM12&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM12 | =G01NHC01BQ001-QM12;XB02 | ELY1 H2 TRT QUAL SV12 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM12 | Solenoid valve | XB02 | Check back off/closed | Ely1 | H2 TRT | QUAL | SV12 | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:18 | 18d | 15 | =G01NHC01BQ001-QM12&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM12 | =G01NHC01BQ001-QM12;YB11 | ELY1 H2 TRT QUAL SV12 CMD ON/OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM12 | Solenoid valve | YB11 | Manual command ON/OPEN | Ely1 | H2 TRT | QUAL | SV12 | CMD ON/OP | -QM12MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DO | 0 | YS | [14 empty] | Not defined | =G01NHY01KF001+U012UNA01UH100-KF09 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 04 | =G01NHC01BQ001-QM12&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM13 | =G01NHC01BQ001-QM13;XB01 | ELY1 H2 TRT QUAL SV13 CB ON/OPN | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM13 | Solenoid valve | XB01 | Check back on/open | Ely1 | H2 TRT | QUAL | SV13 | CB ON/OPN | -QM13BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:37 | 37B | 04 | =G01NHC01BQ001-QM13&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM13 | =G01NHC01BQ001-QM13;XB02 | ELY1 H2 TRT QUAL SV13 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM13 | Solenoid valve | XB02 | Check back off/closed | Ely1 | H2 TRT | QUAL | SV13 | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:19 | 19d | 16 | =G01NHC01BQ001-QM13&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM13 | =G01NHC01BQ001-QM13;YB11 | ELY1 H2 TRT QUAL SV13 CMD ON/OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM13 | Solenoid valve | YB11 | Manual command ON/OPEN | Ely1 | H2 TRT | QUAL | SV13 | CMD ON/OP | -QM13MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DO | 0 | YS | [14 empty] | Not defined | =G01NHY01KF001+U012UNA01UH100-KF09 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 05 | =G01NHC01BQ001-QM13&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM14 | =G01NHC01BQ001-QM14;XB01 | ELY1 H2 TRT QUAL SV14 CB ON/OPN | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM14 | Solenoid valve | XB01 | Check back on/open | Ely1 | H2 TRT | QUAL | SV14 | CB ON/OPN | -QM14BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:42 | 42B | 05 | =G01NHC01BQ001-QM14&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM14 | =G01NHC01BQ001-QM14;XB02 | ELY1 H2 TRT QUAL SV14 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM14 | Solenoid valve | XB02 | Check back off/closed | Ely1 | H2 TRT | QUAL | SV14 | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:20 | 20d | 17 | =G01NHC01BQ001-QM14&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM14 | =G01NHC01BQ001-QM14;YB11 | ELY1 H2 TRT QUAL SV14 CMD ON/OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM14 | Solenoid valve | YB11 | Manual command ON/OPEN | Ely1 | H2 TRT | QUAL | SV14 | CMD ON/OP | -QM14MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DO | 0 | YS | [14 empty] | Not defined | =G01NHY01KF001+U012UNA01UH100-KF09 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 06 | =G01NHC01BQ001-QM14&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM15 | =G01NHC01BQ001-QM15;XB01 | ELY1 H2 TRT QUAL SV15 CB ON/OPN | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM15 | Solenoid valve | XB01 | Check back on/open | Ely1 | H2 TRT | QUAL | SV15 | CB ON/OPN | -QM15BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:47 | 47B | 06 | =G01NHC01BQ001-QM15&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM15 | =G01NHC01BQ001-QM15;XB02 | ELY1 H2 TRT QUAL SV15 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM15 | Solenoid valve | XB02 | Check back off/closed | Ely1 | H2 TRT | QUAL | SV15 | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:21 | 21 | 18 | =G01NHC01BQ001-QM15&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM15 | =G01NHC01BQ001-QM15;YB11 | ELY1 H2 TRT QUAL SV15 CMD ON/OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM15 | Solenoid valve | YB11 | Manual command ON/OPEN | Ely1 | H2 TRT | QUAL | SV15 | CMD ON/OP | -QM15MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DO | 0 | YS | [14 empty] | Not defined | =G01NHY01KF001+U012UNA01UH100-KF09 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 07 | =G01NHC01BQ001-QM15&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM16 | =G01NHC01BQ001-QM16;XB01 | ELY1 H2 TRT QUAL SV16 CB ON/OPN | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM16 | Solenoid valve | XB01 | Check back on/open | Ely1 | H2 TRT | QUAL | SV16 | CB ON/OPN | -QM16BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:52 | 52B | 07 | =G01NHC01BQ001-QM16&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM16 | =G01NHC01BQ001-QM16;XB02 | ELY1 H2 TRT QUAL SV16 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM16 | Solenoid valve | XB02 | Check back off/closed | Ely1 | H2 TRT | QUAL | SV16 | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:23 | 23d | 19 | =G01NHC01BQ001-QM16&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM16 | =G01NHC01BQ001-QM16;YB11 | ELY1 H2 TRT QUAL SV16 CMD ON/OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM16 | Solenoid valve | YB11 | Manual command ON/OPEN | Ely1 | H2 TRT | QUAL | SV16 | CMD ON/OP | -QM16MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DO | 0 | YS | [14 empty] | Not defined | =G01NHY01KF001+U012UNA01UH100-KF09 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 08 | =G01NHC01BQ001-QM16&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM17 | =G01NHC01BQ001-QM17;XB01 | ELY1 H2 TRT QUAL SV17 CB ON/OPN | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM17 | Solenoid valve | XB01 | Check back on/open | Ely1 | H2 TRT | QUAL | SV17 | CB ON/OPN | -QM17BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:57 | 57B | 08 | =G01NHC01BQ001-QM17&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM17 | =G01NHC01BQ001-QM17;XB02 | ELY1 H2 TRT QUAL SV17 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM17 | Solenoid valve | XB02 | Check back off/closed | Ely1 | H2 TRT | QUAL | SV17 | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:24 | 24d | 20 | =G01NHC01BQ001-QM17&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM17 | =G01NHC01BQ001-QM17;YB11 | ELY1 H2 TRT QUAL SV17 CMD ON/OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM17 | Solenoid valve | YB11 | Manual command ON/OPEN | Ely1 | H2 TRT | QUAL | SV17 | CMD ON/OP | -QM17MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DO | 0 | YS | [14 empty] | Not defined | =G01NHY01KF001+U012UNA01UH100-KF09 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 09 | =G01NHC01BQ001-QM17&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM22 | =G01NHC01BQ001-QM22;XB01 | ELY1 H2 TRT QUAL SV22 CB ON/OPN | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM22 | Solenoid valve | XB01 | Check back on/open | Ely1 | H2 TRT | QUAL | SV22 | CB ON/OPN | -QM22BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 01 | =G01NHC01BQ001-QM22&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM22 | =G01NHC01BQ001-QM22;XB02 | ELY1 H2 TRT QUAL SV22 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM22 | Solenoid valve | XB02 | Check back off/closed | Ely1 | H2 TRT | QUAL | SV22 | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB02 | EA01 | 02 | =G01NHC01BQ001-QM22&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM22 | =G01NHC01BQ001-QM22;YB11 | ELY1 H2 TRT QUAL SV22 CMD ON/OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM22 | Solenoid valve | YB11 | Manual command ON/OPEN | Ely1 | H2 TRT | QUAL | SV22 | CMD ON/OP | -QM22MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DO | 0 | YS | [14 empty] | Not defined | =G01NHY01KF001+U012UNA01UH100-KF09 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 10 | =G01NHC01BQ001-QM22&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM23 | =G01NHC01BQ001-QM23;XB11 | ELY1 H2 TRT QUAL SV23 CB MAN ON/OPN | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM 3-WAY VALVE - CAL-GAS MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM23 | 3-way Valve - Cal-Gas | XB11 | Manual command ON/OPEN | Ely1 | H2 TRT | QUAL | SV23 | CB MAN ON/OPN | -QM23BG01 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DI | 0 | GS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB11 | EA01 | 03 | =G01NHC01BQ001-QM23&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01GT001 | G01NHC01GT001-FL01 | =G01NHC01GT001-FL01;XB01 | ELY1 H2 TRT LEAD OFF SFTY VLV CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM GAS LEAD OFF SYSTEMS GAS LEAD OFF SYSTEM 1 ANGLE SAFETY VALVE CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | GT | Gas Lead off Systems | 001 | Gas Lead off System 1 | -FL01 | Angle safety valve | XB01 | Check back on/open | Ely1 | H2 TRT | Lead Off | Sfty Vlv | CB ON/OPN | -FL01BG01 | Electrical | Namur | Namur | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 08 | =G01NHC01GT001-FL01&EFS.001 | =G01NHC01&MFB.002 |  |  | U012UNA01UH100
=G01NHC01GT001 | G01NHC01GT001-QM01 | =G01NHC01GT001-QM01;XB01 | ELY1 H2 TRT LEAD OFF SV1 CB ON/OPN | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM GAS LEAD OFF SYSTEMS GAS LEAD OFF SYSTEM 1 2-WAY SHUT-OFF VALVE H2 CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | GT | Gas Lead off Systems | 001 | Gas Lead off System 1 | -QM01 | 2-way shut-off valve H2 | XB01 | Check back on/open | Ely1 | H2 TRT | Lead Off | SV1 | CB ON/OPN | -QM01BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 09 | =G01NHC01GT001-QM01&EFS.001 | =G01NHC01&MFB.002 |  |  | U012UNA01UH100
=G01NHC01GT001 | G01NHC01GT001-QM01 | =G01NHC01GT001-QM01;XB02 | ELY1 H2 TRT LEAD OFF SV1 CB OFF/CLD | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM GAS LEAD OFF SYSTEMS GAS LEAD OFF SYSTEM 1 2-WAY SHUT-OFF VALVE H2 CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | GT | Gas Lead off Systems | 001 | Gas Lead off System 1 | -QM01 | 2-way shut-off valve H2 | XB02 | Check back off/closed | Ely1 | H2 TRT | Lead Off | SV1 | CB OFF/CLD | -QM01BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB02 | EA01 | 10 | =G01NHC01GT001-QM01&EFS.001 | =G01NHC01&MFB.002 |  |  | U012UNA01UH100
=G01NHC01GT001 | G01NHC01GT001-QN01 | =G01NHC01GT001-QN01;XU01 | ELY1 H2 TRT LEAD OFF CV1 GRP FLT | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM GAS LEAD OFF SYSTEMS GAS LEAD OFF SYSTEM 1 CONTROL VALVE - H2 PRODUCT GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | GT | Gas Lead off Systems | 001 | Gas Lead off System 1 | -QN01 | Control valve - H2 Product | XU01 | Group fault alarm | Ely1 | H2 TRT | Lead Off | CV1 | GRP FLT | -QN01KF01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | YC | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | EA01 | 11 | =G01NHC01GT001-QN01&EFS.001 | =G01NHC01&MFB.002 |  |  | U012UNA01UH100
=G01NHC01GT001 | G01NHC01GT001-QN02 | =G01NHC01GT001-QN02;XU01 | ELY1 H2 TRT LEAD OFF CV2 GRP FLT | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM GAS LEAD OFF SYSTEMS GAS LEAD OFF SYSTEM 1 CONTROL VALVE - H2 BLOW OFF GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | GT | Gas Lead off Systems | 001 | Gas Lead off System 1 | -QN02 | Control valve - H2 Blow off | XU01 | Group fault alarm | Ely1 | H2 TRT | Lead Off | CV2 | GRP FLT | -QN02KF01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | YC | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | EA01 | 12 | =G01NHC01GT001-QN02&EFS.001 | =G01NHC01&MFB.002 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM24 | =G01NHC01BQ001-QM24;XB01 | ELY1 H2 TRT QUAL SV24 CB ON/OPN | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM24 | Solenoid valve | XB01 | Check back on/open | Ely1 | H2 TRT | QUAL | SV24 | CB ON/OPN | -QM24BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:67 | 67B | 09 | =G01NHC01BQ001-QM24&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM24 | =G01NHC01BQ001-QM24;XB02 | ELY1 H2 TRT QUAL SV24 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM24 | Solenoid valve | XB02 | Check back off/closed | Ely1 | H2 TRT | QUAL | SV24 | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:25 | 25d | 21 | =G01NHC01BQ001-QM24&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM24 | =G01NHC01BQ001-QM24;YB11 | ELY1 H2 TRT QUAL SV24 CMD ON/OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM24 | Solenoid valve | YB11 | Manual command ON/OPEN | Ely1 | H2 TRT | QUAL | SV24 | CMD ON/OP | -QM24MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DO | 0 | YS | [14 empty] | Not defined | =G01NHY01KF001+U012UNA01UH100-KF09 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 11 | =G01NHC01BQ001-QM24&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM26 | =G01NHC01BQ001-QM26;XB01 | ELY1 H2 TRT QUAL SV26 CB ON/OPN | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM26 | Solenoid valve | XB01 | Check back on/open | Ely1 | H2 TRT | QUAL | SV26 | CB ON/OPN | -QM26BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | XB01 | 04 | =G01NHC01BQ001-QM26&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM26 | =G01NHC01BQ001-QM26;XB02 | ELY1 H2 TRT QUAL SV26 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM26 | Solenoid valve | XB02 | Check back off/closed | Ely1 | H2 TRT | QUAL | SV26 | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB02 | XB02 | 05 | =G01NHC01BQ001-QM26&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM26 | =G01NHC01BQ001-QM26;YB11 | ELY1 H2 TRT QUAL SV26 CMD ON/OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM SOLENOID VALVE MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM26 | Solenoid valve | YB11 | Manual command ON/OPEN | Ely1 | H2 TRT | QUAL | SV26 | CMD ON/OP | -QM26MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DO | 0 | YS | [14 empty] | Not defined | =G01NHY01KF001+U012UNA01UH100-KF09 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 12 | =G01NHC01BQ001-QM26&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QM27 | =G01NHC01BQ001-QM27;XB11 | ELY1 H2 TRT QUAL SV27 CB MAN ON/OPN | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM 3-WAY VALVE - CAL-GAS MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QM27 | 3-way Valve - Cal-Gas | XB11 | Manual command ON/OPEN | Ely1 | H2 TRT | QUAL | SV27 | CB MAN ON/OPN | -QM27BG01 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DI | 0 | GS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB11 | EA01 | 06 | =G01NHC01BQ001-QM27&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QN22 | =G01NHC01BQ001-QN22;XG01 | ELY1 H2 TRT QUAL PRES22 CB ON/OPN/MAX1 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM PRESSURE GAUGE WITH PRESSURE SWITCH CHECK BACK ON/OPEN // LIMIT VALUE >MAX 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QN22 | Pressure gauge with pressure switch | XG01 | Check back on/open // Limit value >max 1 | Ely1 | H2 TRT | QUAL | Pres22 | CB ON/OPN/MAX1 | -QN22 | Electrical | 24 VAC | 24 VAC | Wire | Normally closed |  |  | DI | 0 | PS | [9 empty] | AL | [5 empty] | =G01NHY01KF001+U012UNA01UH100-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XG01 | EA01 | 06 | =G01NHC01BQ001-QN22&EFS.001 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-QN30 | =G01NHC01BQ001-QN30;XW01 | ELY1 H2 TRT QUAL PRES30 AL/FLT CODE | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM PRESSURE GAUGE WITH PRESSURE SWITCH ALARM SYSTEM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -QN30 | Pressure gauge with pressure switch | XW01 | Alarm system | Ely1 | H2 TRT | QUAL | Pres30 | AL/FLT CODE | -QN30 | Electrical | 24 VAC | 24 VAC | Wire | Normally closed |  |  | DI | 1 | PZ | [9 empty] | AZL |  |  |  | Yes |  | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:83 | 83B | 10 | =G01NHC01BQ001-QN30&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01BQ001 | G01NHC01BQ001-SF01 | =G01NHC01BQ001-SF01;XB11 | ELY1 H2 TRT QUAL SW OFF CB MAN ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM QUALITY MEASURING SYSTEM O2 IN H2 MEASURING SYSTEM KEY-SWITCH - MAINTENANCE ON/OFF MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | BQ | Quality Measuring System | 001 | O2 in H2 Measuring System | -SF01 | Key-switch - Maintenance on/off | XB11 | Manual command ON/OPEN | Ely1 | H2 TRT | QUAL | Sw OFF | CB MAN ON/OPN | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DI | 0 | HC | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB11 | EA01 | 07 | =G01NHC01BQ001-SF01&EFS.002 | =G01NHC01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-BF01 | =G01NHE01BQ001-BF01;XG02 | ELY1 O2 TRT QUAL FLOW1 CB ON/OPN/MIN1 | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM 10301; FLOWMETER GENERAL CHECK BACK OFF/CLOSED // LIMIT VALUE >MIN 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -BF01 | 10301; Flowmeter general | XG02 | Check back off/closed // Limit value >min 1 | Ely1 | O2 TRT | QUAL | Flow1 | CB ON/OPN/MIN1 | -BF01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | FSZ | [7 empty] | AH |  | AL |  |  |  | Yes |  | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:1 | 1B | 11 | =G01NHE01BQ001-BF01&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-BF01 | =G01NHE01BQ001-BF01;XG01 | ELY1 O2 TRT QUAL FLOW1 CB ON/OPN/MAX1 | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM 10301; FLOWMETER GENERAL CHECK BACK ON/OPEN // LIMIT VALUE >MAX 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -BF01 | 10301; Flowmeter general | XG01 | Check back on/open // Limit value >max 1 | Ely1 | O2 TRT | QUAL | Flow1 | CB ON/OPN/MAX1 | -BF01 | Electrical | 24 VAC | 24 VAC | Wire | Normally opened |  |  | DI | 0 | FSZ | [7 empty] | AH |  | AL |  |  |  | Yes |  | =G01NHY01KF001+U012UNA01UH100-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XG01 | EA01 | 13 | =G01NHE01BQ001-BF01&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-BF02 | =G01NHE01BQ001-BF02;XG02 | ELY1 O2 TRT QUAL FLOW2 CB ON/OPN/MIN1 | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM 10301; FLOWMETER GENERAL CHECK BACK OFF/CLOSED // LIMIT VALUE >MIN 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -BF02 | 10301; Flowmeter general | XG02 | Check back off/closed // Limit value >min 1 | Ely1 | O2 TRT | QUAL | Flow2 | CB ON/OPN/MIN1 | -BF02 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | FSZ | [7 empty] | AH |  | AL |  |  |  | Yes |  | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:5 | 5B | 23 | =G01NHE01BQ001-BF02&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-BF02 | =G01NHE01BQ001-BF02;XG01 | ELY1 O2 TRT QUAL FLOW2 CB ON/OPN/MAX1 | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM 10301; FLOWMETER GENERAL CHECK BACK ON/OPEN // LIMIT VALUE >MAX 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -BF02 | 10301; Flowmeter general | XG01 | Check back on/open // Limit value >max 1 | Ely1 | O2 TRT | QUAL | Flow2 | CB ON/OPN/MAX1 | -BF02 | Electrical | 24 VAC | 24 VAC | Wire | Normally opened |  |  | DI | 0 | FSZ | [7 empty] | AH |  | AL |  |  |  | Yes |  | =G01NHY01KF001+U012UNA01UH100-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XG01 | EA01 | 14 | =G01NHE01BQ001-BF02&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-BF10 | =G01NHE01BQ001-BF10;XG02 | ELY1 O2 TRT QUAL FLOW1 CB ON/OPN/MIN1 | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM 10301; FLOWMETER GENERAL CHECK BACK OFF/CLOSED // LIMIT VALUE >MIN 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -BF10 | 10301; Flowmeter general | XG02 | Check back off/closed // Limit value >min 1 | Ely1 | O2 TRT | QUAL | Flow1 | CB ON/OPN/MIN1 | -BF10 | Electrical | 24 VAC | 24 VAC | Wire | Normally opened |  |  | DI | 0 | FS | [9 empty] | AL | [5 empty] | =G01NHY01KF001+U012UNA01UH100-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XG02 | EA01 | 15 | =G01NHE01BQ001-BF10&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-BP10 | =G01NHE01BQ001-BP10;XG01 | ELY1 O2 TRT QUAL PRES SW CB ON/OPN/MAX1 | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM PRESSURE SWITCH CHECK BACK ON/OPEN // LIMIT VALUE >MAX 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -BP10 | Pressure switch | XG01 | Check back on/open // Limit value >max 1 | Ely1 | O2 TRT | QUAL | Pres sw | CB ON/OPN/MAX1 | -BP10 | Electrical | 24 VAC | 24 VAC | Wire | Undefined |  |  | DI | 0 | PIS | [9 empty] | AL | [5 empty] | =G01NHY01KF001+U012UNA01UH100-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XG01 | EA01 | 01 | =G01NHE01BQ001-BP10&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-BQ01 | =G01NHE01BQ001-BQ01;XQ01 | ELY1 O2 TRT QUAL QUAL1 ANALOG1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM H2-MEASURING SENSOR ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -BQ01 | H2-measuring sensor | XQ01 | Analog process signal | Ely1 | O2 TRT | QUAL | Qual1 | ANALOG1 | -BQ01 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | AI | [5 empty] | ASHH |  | AH | [5 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF06 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | XG06:12 | 12d | 06 | =G01NHE01BQ001-BQ01&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-BQ01 | =G01NHE01BQ001-BQ01;XM01 | ELY1 O2 TRT QUAL QUAL1 AL1 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM H2-MEASURING SENSOR FAULT | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -BQ01 | H2-measuring sensor | XM01 | Fault | Ely1 | O2 TRT | QUAL | Qual1 | AL1 | -BQ01 | Electrical | 24 VAC | 24 VAC | Wire | Normally closed |  |  | DI | 0 | XS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XM01 | EA01 | 03 | =G01NHE01BQ001-BQ01&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-BQ01 | =G01NHE01BQ001-BQ01;XJ01 | ELY1 O2 TRT QUAL QUAL1 RDY F OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM H2-MEASURING SENSOR FUNCTIONAL CHECK | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -BQ01 | H2-measuring sensor | XJ01 | Functional check | Ely1 | O2 TRT | QUAL | Qual1 | RDY F OP | -BQ01 | Electrical | 24 VAC | 24 VAC | Wire | Normally closed |  |  | DI | 0 | XS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XJ01 | EA01 | 02 | =G01NHE01BQ001-BQ01&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-BQ02 | =G01NHE01BQ001-BQ02;XQ01 | ELY1 O2 TRT QUAL QUAL2 ANALOG1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM H2-MEASURING SENSOR ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -BQ02 | H2-measuring sensor | XQ01 | Analog process signal | Ely1 | O2 TRT | QUAL | Qual2 | ANALOG1 | -BQ02 | Electrical | 4..20 mA | 4..20 mA | Wire | Continuous signal |  |  | AI | 1 | AI | [5 empty] | ASHH |  | AH | [5 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF07 | 6ES7 336-4GE00-0AB0, SM 336, 6AI, 0/4-20mA, failsafe | XG07:2 | 2d | 01 | =G01NHE01BQ001-BQ02&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-BQ02 | =G01NHE01BQ001-BQ02;XM01 | ELY1 O2 TRT QUAL QUAL2 AL1 | 26 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM H2-MEASURING SENSOR FAULT | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -BQ02 | H2-measuring sensor | XM01 | Fault | Ely1 | O2 TRT | QUAL | Qual2 | AL1 | -BQ02 | Electrical | 24 VAC | 24 VAC | Wire | Normally closed |  |  | DI | 0 | XS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XM01 | EA01 | 05 | =G01NHE01BQ001-BQ02&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-BQ02 | =G01NHE01BQ001-BQ02;XJ01 | ELY1 O2 TRT QUAL QUAL2 RDY F OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM H2-MEASURING SENSOR FUNCTIONAL CHECK | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -BQ02 | H2-measuring sensor | XJ01 | Functional check | Ely1 | O2 TRT | QUAL | Qual2 | RDY F OP | -BQ02 | Electrical | 24 VAC | 24 VAC | Wire | Normally closed |  |  | DI | 0 | XS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XJ01 | EA01 | 04 | =G01NHE01BQ001-BQ02&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-EQ01 | =G01NHE01BQ001-EQ01;XU01 | ELY1 O2 TRT QUAL GAS COOL GRP FLT | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM GAS COOLER O2 GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -EQ01 | Gas Cooler O2 | XU01 | Group fault alarm | Ely1 | O2 TRT | QUAL | Gas Cool | GRP FLT | X?? | Electrical | 24 VAC | 24 VAC | Wire | Undefined |  |  | DI | 0 | XS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | EA01 | 07 | =G01NHE01BQ001-EQ01&EFS.002 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-EQ01 | =G01NHE01BQ001-EQ01;XB13 | ELY1 O2 TRT QUAL GAS COOL CHECK CMD | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM GAS COOLER O2 CHECK COMMAND | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -EQ01 | Gas Cooler O2 | XB13 | Check command | Ely1 | O2 TRT | QUAL | Gas Cool | Check CMD |  | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | NS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10_1:XB13 | EA01 | 06 | =G01NHE01BQ001-EQ01&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-EQ01 | =G01NHE01BQ001-EQ01;YB11 | ELY1 O2 TRT QUAL GAS COOL CMD ON/OP | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM GAS COOLER O2 MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -EQ01 | Gas Cooler O2 | YB11 | Manual command ON/OPEN | Ely1 | O2 TRT | QUAL | Gas Cool | CMD ON/OP | -XG01 | Electrical | 24 VAC | 24 VAC | Wire | Undefined |  |  | DO | 0 | NS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF09 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10_1:YB11 | EA01 | 15 | =G01NHE01BQ001-EQ01&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-FC01 | =G01NHE01BQ001-FC01;XU01 | ELY1 O2 TRT QUAL 24V MON1 GRP FLT | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM GENERAL FEEDBACK - POWER SUPPLY GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -FC01 | General Feedback - Power Supply | XU01 | Group fault alarm | Ely1 | O2 TRT | QUAL | 24V MON1 | GRP FLT | -XG01 | Electrical | 24 VAC | 24 VAC | Wire | Undefined |  |  | DI | 0 | XS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | EA01 | 08 | =G01NHE01BQ001-FC01&EFS.002 |  |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-GP01 | =G01NHE01BQ001-GP01;XB13 | ELY1 O2 TRT QUAL PMP1 CHECK CMD | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM GAS ANALYTIC PUMP, O2 CHECK COMMAND | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -GP01 | Gas Analytic Pump, O2 | XB13 | Check command | Ely1 | O2 TRT | QUAL | PMP1 | Check CMD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | NS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10_1:XB13 | EA01 | 09 | =G01NHE01BQ001-GP01&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-GP01 | =G01NHE01BQ001-GP01;YB11 | ELY1 O2 TRT QUAL PMP1 CMD ON/OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM GAS ANALYTIC PUMP, O2 MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -GP01 | Gas Analytic Pump, O2 | YB11 | Manual command ON/OPEN | Ely1 | O2 TRT | QUAL | PMP1 | CMD ON/OP | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 0 | NS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF09 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10_1:YB11 | EA01 | 14 | =G01NHE01BQ001-GP01&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM11 | =G01NHE01BQ001-QM11;XB01 | ELY1 O2 TRT QUAL SV11 CB ON/OPN | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM11 | Solenoid valve | XB01 | Check back on/open | Ely1 | O2 TRT | QUAL | SV11 | CB ON/OPN | -QM11BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:27 | 27B | 12 | =G01NHE01BQ001-QM11&EFS.002 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM11 | =G01NHE01BQ001-QM11;XB02 | ELY1 O2 TRT QUAL SV11 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM11 | Solenoid valve | XB02 | Check back off/closed | Ely1 | O2 TRT | QUAL | SV11 | CB OFF/CLD | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF01 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:28 | 28d | 24 | =G01NHE01BQ001-QM11&EFS.002 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM11 | =G01NHE01BQ001-QM11;YB11 | ELY1 O2 TRT QUAL SV11 CMD ON/OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM11 | Solenoid valve | YB11 | Manual command ON/OPEN | Ely1 | O2 TRT | QUAL | SV11 | CMD ON/OP | -QM11MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DO | 0 | YS | [14 empty] | Not defined | =G01NHY01KF001+U012UNA01UH100-KF09 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 16 | =G01NHE01BQ001-QM11&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM12 | =G01NHE01BQ001-QM12;XB01 | ELY1 O2 TRT QUAL SV12 CB ON/OPN | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM12 | Solenoid valve | XB01 | Check back on/open | Ely1 | O2 TRT | QUAL | SV12 | CB ON/OPN | -QM12BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF02 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:32 | 32B | 01 | =G01NHE01BQ001-QM12&EFS.002 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01GT001 | G01NHE01GT001-FL01 | =G01NHE01GT001-FL01;XB01 | ELY1 O2 TRT LEAD OFF SFTY VLV CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM GAS LEAD OFF SYSTEMS GAS LEAD OFF SYSTEM 1 ANGLE SAFETY VALVE CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | GT | Gas Lead off Systems | 001 | Gas Lead off System 1 | -FL01 | Angle safety valve | XB01 | Check back on/open | Ely1 | O2 TRT | Lead Off | Sfty Vlv | CB ON/OPN | -FL01BG01 | Electrical | Namur | Namur | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 16 | =G01NHE01GT001-FL01&EFS.001 | =G01NHE01&MFB.002 |  |  | U012UNA01UH100
=G01NHE01GT001 | G01NHE01GT001-QN01 | =G01NHE01GT001-QN01;XU01 | ELY1 O2 TRT LEAD OFF CV1 GRP FLT | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM GAS LEAD OFF SYSTEMS GAS LEAD OFF SYSTEM 1 CONTROL VALVE - O2 BLOW OFF GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | GT | Gas Lead off Systems | 001 | Gas Lead off System 1 | -QN01 | Control valve - O2 Blow off | XU01 | Group fault alarm | Ely1 | O2 TRT | Lead Off | CV1 | GRP FLT | -QN01KF01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | YC | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | EA01 | 01 | =G01NHE01GT001-QN01&EFS.001 | =G01NHE01&MFB.002 |  |  | U012UNA01UH100
=G01NHG01QM001 | G01NHG01QM001-QM01 | =G01NHG01QM001-QM01;XB01 | ELY1 PROC WTR SUP DIST SV1 CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 WATER SUPPLY SYSTEMS PROCESS WATER SUPPLY SYSTEM PROCESS WATER DISTRIBUTION SYSTEMS PROCESS WATER DISTRIBUTION SYSTEM 2-WAY SHUT-OFF VALVE - DEMIN WATER SUPPLY CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHG | Water Supply Systems | 01 | Process Water Supply System | QM | Process Water Distribution Systems | 001 | Process Water Distribution System | -QM01 | 2-way shut-off valve - Demin water supply | XB01 | Check back on/open | Ely1 | Proc Wtr Sup | DIST | SV1 | CB ON/OPN | -QM01BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 02 | =G01NHG01QM001-QM01&EFS.001 | =G01NHC01&MFB.001 |  |  | U012UNA01UH100
=G01NHG01QM001 | G01NHG01QM001-QM01 | =G01NHG01QM001-QM01;XB02 | ELY1 PROC WTR SUP DIST SV1 CB OFF/CLD | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 WATER SUPPLY SYSTEMS PROCESS WATER SUPPLY SYSTEM PROCESS WATER DISTRIBUTION SYSTEMS PROCESS WATER DISTRIBUTION SYSTEM 2-WAY SHUT-OFF VALVE - DEMIN WATER SUPPLY CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHG | Water Supply Systems | 01 | Process Water Supply System | QM | Process Water Distribution Systems | 001 | Process Water Distribution System | -QM01 | 2-way shut-off valve - Demin water supply | XB02 | Check back off/closed | Ely1 | Proc Wtr Sup | DIST | SV1 | CB OFF/CLD | -QM01BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB02 | EA01 | 03 | =G01NHG01QM001-QM01&EFS.001 | =G01NHC01&MFB.001 |  |  | U012UNA01UH100
=G01NHG01QM001 | G01NHG01QM001-QN01 | =G01NHG01QM001-QN01;XU01 | ELY1 PROC WTR SUP DIST CV1 GRP FLT | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 WATER SUPPLY SYSTEMS PROCESS WATER SUPPLY SYSTEM PROCESS WATER DISTRIBUTION SYSTEMS PROCESS WATER DISTRIBUTION SYSTEM CONTROL VALVE - DEMIN WATER SUPPLY GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHG | Water Supply Systems | 01 | Process Water Supply System | QM | Process Water Distribution Systems | 001 | Process Water Distribution System | -QN01 | Control valve - Demin Water Supply | XU01 | Group fault alarm | Ely1 | Proc Wtr Sup | DIST | CV1 | GRP FLT | -QN01KF01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | YC | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | EA01 | 04 | =G01NHG01QM001-QN01&EFS.001 | =G01NHC01&MFB.001 |  |  | U012UNA01UH100
=G01NHP01WP001 | G01NHP01WP001-QN01 | =G01NHP01WP001-QN01;XU01 | ELY1 HEAT DISS PIPING CV1 GRP FLT | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 HEAT DISSIPATION SYSTEMS HEAT DISSIPATION (ELECTROLYSER SYSTEM) DISTRIBUTION COOLING WATER (ELECTROLYSER SYSTEM) PLANT COOLING WATER PIPE SYSTEM CONTROL VALVE - GAS COOLER H2 COOLING WATER GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHP | Heat Dissipation Systems | 01 | Heat dissipation (Electrolyser System) | WP | Distribution Cooling Water (Electrolyser System) | 001 | Plant Cooling Water Pipe System | -QN01 | Control Valve - Gas Cooler H2 Cooling Water | XU01 | Group fault alarm | Ely1 | Heat Diss | Piping | CV1 | GRP FLT | -QN01KF01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | YC | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | EA01 | 05 | =G01NHP01WP001-QN01&EFS.001 | =G01NHC01&MFB.002 |  |  | U012UNA01UH100
=G01NHP01WP001 | G01NHP01WP001-QN02 | =G01NHP01WP001-QN02;XU01 | ELY1 HEAT DISS PIPING CV2 GRP FLT | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 HEAT DISSIPATION SYSTEMS HEAT DISSIPATION (ELECTROLYSER SYSTEM) DISTRIBUTION COOLING WATER (ELECTROLYSER SYSTEM) PLANT COOLING WATER PIPE SYSTEM CONTROL VALVE - GAS COOLER O2 COOLING WATER GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHP | Heat Dissipation Systems | 01 | Heat dissipation (Electrolyser System) | WP | Distribution Cooling Water (Electrolyser System) | 001 | Plant Cooling Water Pipe System | -QN02 | Control Valve - Gas Cooler O2 Cooling Water | XU01 | Group fault alarm | Ely1 | Heat Diss | Piping | CV2 | GRP FLT | -QN02KF01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | YC | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | EA01 | 06 | =G01NHP01WP001-QN02&EFS.001 | =G01NHE01&MFB.002 |  |  | U012UNA01UH100
=G01NHX01QN001 | G01NHX01QN001-QM11 | =G01NHX01QN001-QM11;XB11 | ELY1 N2 DIST CTRL H2 SV11 CB MAN ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION H2 BALL VALVE - NITROGEN H2 BYPASS MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 001 | Nitrogen Regulation H2 | -QM11 | Ball valve - Nitrogen H2 bypass | XB11 | Manual command ON/OPEN | Ely1 | N2 Dist | CTRL H2 | SV11 | CB MAN ON/OPN | -QM11BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB11 | EA01 | 07 | =G01NHX01QN001-QM11&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=G01NHX01QN001 | G01NHX01QN001-QM11 | =G01NHX01QN001-QM11;XB12 | ELY1 N2 DIST CTRL H2 SV11 CB MAN OFF/CLD | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION H2 BALL VALVE - NITROGEN H2 BYPASS MANUAL COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 001 | Nitrogen Regulation H2 | -QM11 | Ball valve - Nitrogen H2 bypass | XB12 | Manual command OFF/CLOSE | Ely1 | N2 Dist | CTRL H2 | SV11 | CB MAN OFF/CLD | -QM11BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB12 | EA01 | 08 | =G01NHX01QN001-QM11&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=G01NHX01QN001 | G01NHX01QN001-QM21 | =G01NHX01QN001-QM21;XB11 | ELY1 N2 DIST CTRL H2 SV21 CB MAN ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION H2 BALL VALVE - NITROGEN H2 OUTLET MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 001 | Nitrogen Regulation H2 | -QM21 | Ball valve - Nitrogen H2 outlet | XB11 | Manual command ON/OPEN | Ely1 | N2 Dist | CTRL H2 | SV21 | CB MAN ON/OPN | -QM21BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB11 | EA01 | 09 | =G01NHX01QN001-QM21&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=G01NHX01QN001 | G01NHX01QN001-QM21 | =G01NHX01QN001-QM21;XB12 | ELY1 N2 DIST CTRL H2 SV21 CB MAN OFF/CLD | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION H2 BALL VALVE - NITROGEN H2 OUTLET MANUAL COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 001 | Nitrogen Regulation H2 | -QM21 | Ball valve - Nitrogen H2 outlet | XB12 | Manual command OFF/CLOSE | Ely1 | N2 Dist | CTRL H2 | SV21 | CB MAN OFF/CLD | -QM21BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB12 | EA01 | 10 | =G01NHX01QN001-QM21&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=G01NHX01QN001 | G01NHX01QN001-QN01 | =G01NHX01QN001-QN01;XU01 | ELY1 N2 DIST CTRL H2 CV1 GRP FLT | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION H2 CONTROL VALVE - NITROGEN H2 SIDE GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 001 | Nitrogen Regulation H2 | -QN01 | Control valve - Nitrogen H2 side | XU01 | Group fault alarm | Ely1 | N2 Dist | CTRL H2 | CV1 | GRP FLT | -QN01KF01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | EA01 | 11 | =G01NHX01QN001-QN01&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=G01NHX01QN002 | G01NHX01QN002-QM11 | =G01NHX01QN002-QM11;XB11 | ELY1 N2 DIST CTRL O2 SV11 CB MAN ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION O2 BALL VALVE - NITROGEN O2 BYPASS MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 002 | Nitrogen Regulation O2 | -QM11 | Ball valve - Nitrogen O2 bypass | XB11 | Manual command ON/OPEN | Ely1 | N2 Dist | CTRL O2 | SV11 | CB MAN ON/OPN | -QM11BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB11 | EA01 | 12 | =G01NHX01QN002-QM11&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=G01NHX01QN002 | G01NHX01QN002-QM11 | =G01NHX01QN002-QM11;XB12 | ELY1 N2 DIST CTRL O2 SV11 CB MAN OFF/CLD | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION O2 BALL VALVE - NITROGEN O2 BYPASS MANUAL COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 002 | Nitrogen Regulation O2 | -QM11 | Ball valve - Nitrogen O2 bypass | XB12 | Manual command OFF/CLOSE | Ely1 | N2 Dist | CTRL O2 | SV11 | CB MAN OFF/CLD | -QM11BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB12 | EA01 | 13 | =G01NHX01QN002-QM11&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=G01NHX01QN002 | G01NHX01QN002-QM21 | =G01NHX01QN002-QM21;XB11 | ELY1 N2 DIST CTRL O2 SV21 CB MAN ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION O2 BALL VALVE - NITROGEN O2 OUTLET MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 002 | Nitrogen Regulation O2 | -QM21 | Ball valve - Nitrogen O2 outlet | XB11 | Manual command ON/OPEN | Ely1 | N2 Dist | CTRL O2 | SV21 | CB MAN ON/OPN | -QM21BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB11 | EA01 | 14 | =G01NHX01QN002-QM21&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=G01NHX01QN002 | G01NHX01QN002-QM21 | =G01NHX01QN002-QM21;XB12 | ELY1 N2 DIST CTRL O2 SV21 CB MAN OFF/CLD | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION O2 BALL VALVE - NITROGEN O2 OUTLET MANUAL COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 002 | Nitrogen Regulation O2 | -QM21 | Ball valve - Nitrogen O2 outlet | XB12 | Manual command OFF/CLOSE | Ely1 | N2 Dist | CTRL O2 | SV21 | CB MAN OFF/CLD | -QM21BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB12 | EA01 | 15 | =G01NHX01QN002-QM21&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=G01NHX01QN002 | G01NHX01QN002-QN01 | =G01NHX01QN002-QN01;XU01 | ELY1 N2 DIST CTRL O2 CV1 GRP FLT | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION O2 CONTROL VALVE - NITROGEN O2 SIDE GROUP FAULT ALARM | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 002 | Nitrogen Regulation O2 | -QN01 | Control valve - Nitrogen O2 side | XU01 | Group fault alarm | Ely1 | N2 Dist | CTRL O2 | CV1 | GRP FLT | -QN01KF01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XU01 | EA01 | 16 | =G01NHX01QN002-QN01&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-BA11 | =G01NHY01KF001-BA11;XB01 | ELY1 ARY CTRL U1 400VAC MON CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 400VAC MONITORING CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -BA11 | 400VAC Monitoring | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 400VAC MON | CB ON/OPN | 1 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF06 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 01 | =G01NHY01KF001-BA11&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-BA21 | =G01NHY01KF001-BA21;XB01 | ELY1 ARY CTRL U1 230VAC MON CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 2300VAC MONITORING CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -BA21 | 2300VAC Monitoring | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 230VAC MON | CB ON/OPN | 1 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF06 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 02 | =G01NHY01KF001-BA21&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-BA41 | =G01NHY01KF001-BA41;XB01 | ELY1 ARY CTRL U1 UPS MON CB ON/OPN | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 230VAC UPS MONITORING CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -BA41 | 230VAC UPS Monitoring | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | UPS MON | CB ON/OPN | 1 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF06 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 03 | =G01NHY01KF001-BA41&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC01 | =G01NHY01KF001-FC01;XB01 | ELY1 ARY CTRL U1 24V MON1 CB ON/OPN | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 24VDC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC01 | 24VDC Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 24V MON1 | CB ON/OPN | -FC01 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF06 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 04 | =G01NHY01KF001-FC01&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC02 | =G01NHY01KF001-FC02;XB01 | ELY1 ARY CTRL U1 24V MON2 CB ON/OPN | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 24VDC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC02 | 24VDC Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 24V MON2 | CB ON/OPN | -FC02 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF06 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 05 | =G01NHY01KF001-FC02&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC03 | =G01NHY01KF001-FC03;XB01 | ELY1 ARY CTRL U1 24V MON3 CB ON/OPN | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 24VDC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC03 | 24VDC Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 24V MON3 | CB ON/OPN | -FC03 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF06 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 06 | =G01NHY01KF001-FC03&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC11 | =G01NHY01KF001-FC11;XB01 | ELY1 ARY CTRL U1 400VAC IN CB ON/OPN | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 400VAC INPUT CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC11 | 400VAC Input | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 400VAC In | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF06 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 07 | =G01NHY01KF001-FC11&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC21 | =G01NHY01KF001-FC21;XB01 | ELY1 ARY CTRL U1 230VAC1 CB ON/OPN | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC21 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 230VAC1 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF06 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 08 | =G01NHY01KF001-FC21&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC22 | =G01NHY01KF001-FC22;XB01 | ELY1 ARY CTRL U1 230VAC2 CB ON/OPN | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC22 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 230VAC2 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF06 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 09 | =G01NHY01KF001-FC22&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC23 | =G01NHY01KF001-FC23;XB01 | ELY1 ARY CTRL U1 230VAC3 CB ON/OPN | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC23 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 230VAC3 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF06 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 10 | =G01NHY01KF001-FC23&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC24 | =G01NHY01KF001-FC24;XB01 | ELY1 ARY CTRL U1 230VAC4 CB ON/OPN | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC24 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 230VAC4 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF06 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 11 | =G01NHY01KF001-FC24&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC25 | =G01NHY01KF001-FC25;XB01 | ELY1 ARY CTRL U1 230VAC5 CB ON/OPN | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC25 | 230VAC Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 230VAC5 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF06 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 12 | =G01NHY01KF001-FC25&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC41 | =G01NHY01KF001-FC41;XB01 | ELY1 ARY CTRL U1 230VAC UPS1 CB ON/OPN | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC41 | 230VAC UPS Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 230VAC UPS1 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF06 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 13 | =G01NHY01KF001-FC41&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC42 | =G01NHY01KF001-FC42;XB01 | ELY1 ARY CTRL U1 230VAC UPS2 CB ON/OPN | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC42 | 230VAC UPS Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 230VAC UPS2 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF06 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 14 | =G01NHY01KF001-FC42&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC43 | =G01NHY01KF001-FC43;XB01 | ELY1 ARY CTRL U1 230VAC UPS3 CB ON/OPN | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC43 | 230VAC UPS Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 230VAC UPS3 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF06 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 15 | =G01NHY01KF001-FC43&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC44 | =G01NHY01KF001-FC44;XB01 | ELY1 ARY CTRL U1 230VAC UPS4 CB ON/OPN | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC44 | 230VAC UPS Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 230VAC UPS4 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF06 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 16 | =G01NHY01KF001-FC44&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC45 | =G01NHY01KF001-FC45;XB01 | ELY1 ARY CTRL U1 230VAC UPS5 CB ON/OPN | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC45 | 230VAC UPS Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 230VAC UPS5 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF07 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 01 | =G01NHY01KF001-FC45&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC46 | =G01NHY01KF001-FC46;XB01 | ELY1 ARY CTRL U1 230VAC UPS6 CB ON/OPN | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC46 | 230VAC UPS Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 230VAC UPS6 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF07 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 02 | =G01NHY01KF001-FC46&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC47 | =G01NHY01KF001-FC47;XB01 | ELY1 ARY CTRL U1 230VAC UPS7 CB ON/OPN | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC47 | 230VAC UPS Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 230VAC UPS7 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF07 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 03 | =G01NHY01KF001-FC47&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC48 | =G01NHY01KF001-FC48;XB01 | ELY1 ARY CTRL U1 230VAC UPS8 CB ON/OPN | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC48 | 230VAC UPS Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 230VAC UPS8 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF07 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 04 | =G01NHY01KF001-FC48&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC49 | =G01NHY01KF001-FC49;XB01 | ELY1 ARY CTRL U1 230VAC UPS9 CB ON/OPN | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC49 | 230VAC UPS Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 230VAC UPS9 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF07 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 05 | =G01NHY01KF001-FC49&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC50 | =G01NHY01KF001-FC50;XB01 | ELY1 ARY CTRL U1 230VAC UPS10 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC50 | 230VAC UPS Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 230VAC UPS10 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF07 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 06 | =G01NHY01KF001-FC50&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC51 | =G01NHY01KF001-FC51;XB01 | ELY1 ARY CTRL U1 230VAC UPS11 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC51 | 230VAC UPS Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 230VAC UPS11 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF07 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 07 | =G01NHY01KF001-FC51&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC52 | =G01NHY01KF001-FC52;XB01 | ELY1 ARY CTRL U1 230VAC UPS12 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC52 | 230VAC UPS Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 230VAC UPS12 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF07 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 08 | =G01NHY01KF001-FC52&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-FC53 | =G01NHY01KF001-FC53;XB01 | ELY1 ARY CTRL U1 230VAC UPS13 CB ON/OPN | 39 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -FC53 | 230VAC UPS Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 230VAC UPS13 | CB ON/OPN |  | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF07 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 09 | =G01NHY01KF001-FC53&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-QA11 | =G01NHY01KF001-QA11;XB01 | ELY1 ARY CTRL U1 SW 400VAC1 CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -QA11 | 400VAC Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | Sw 400VAC1 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF07 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 10 | =G01NHY01KF001-QA11&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-QA12 | =G01NHY01KF001-QA12;XB01 | ELY1 ARY CTRL U1 SW 400VAC2 CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -QA12 | 400VAC Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | Sw 400VAC2 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF07 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 11 | =G01NHY01KF001-QA12&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-QA13 | =G01NHY01KF001-QA13;XB01 | ELY1 ARY CTRL U1 SW 400VAC3 CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -QA13 | 400VAC Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | Sw 400VAC3 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF07 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 12 | =G01NHY01KF001-QA13&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-QA14 | =G01NHY01KF001-QA14;XB01 | ELY1 ARY CTRL U1 SW 400VAC4 CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -QA14 | 400VAC Distribution | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | Sw 400VAC4 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF07 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 13 | =G01NHY01KF001-QA14&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-SF01 | =G01NHY01KF001-SF01;XW02 | ELY1 ARY CTRL U1 SW OFF WARN CODE | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT EMERGENCY STOP - PUSHBUTTON - CABINET I&C ELECTROLYSIS ARRAY COMPONENT PROTECTION | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -SF01 | Emergency Stop - Pushbutton - Cabinet I&C Electrolysis Array | XW02 | Component protection | Ely1 | Ary | CTRL U1 | Sw OFF | WARN CODE | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF02 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | B10:XW02 | XW02 | 18 | =G01NHY01KF001-SF01&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-SF01 | =G01NHY01KF001-SF01;XW01 | ELY1 ARY CTRL U1 SW OFF AL/FLT CODE | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT EMERGENCY STOP - PUSHBUTTON - CABINET I&C ELECTROLYSIS ARRAY COMPONENT PROTECTION | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -SF01 | Emergency Stop - Pushbutton - Cabinet I&C Electrolysis Array | XW01 | Component protection | Ely1 | Ary | CTRL U1 | Sw OFF | AL/FLT CODE | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF02 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | B10:XW01 | XW01 | 06 | =G01NHY01KF001-SF01&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-TB01 | =G01NHY01KF001-TB01;XB01 | ELY1 ARY CTRL U1 24VDC MON1 CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT SITOP PSU6200 24 V/20 A CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -TB01 | SITOP PSU6200 24 V/20 A | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 24VDC MON1 | CB ON/OPN | 1 | Electrical | 24 VDC | 24 VDC | Wire | Continuous signal |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF07 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 14 | =G01NHY01KF001-TB01&EFS.001 |  |  |  | U012UNA01UH100
=G01NHY01KF001 | G01NHY01KF001-TB02 | =G01NHY01KF001-TB02;XB01 | ELY1 ARY CTRL U1 24VDC MON2 CB ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ARRAY CONTROL SYSTEM ARRAY CONTROL SYSTEM CONTROL UNITS ARRAY CONTROL UNIT SITOP PSU6200 24 V/20 A CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHY | Array Control System | 01 | Array Control System | KF | Control Units | 001 | Array Control Unit | -TB02 | SITOP PSU6200 24 V/20 A | XB01 | Check back on/open | Ely1 | Ary | CTRL U1 | 24VDC MON2 | CB ON/OPN | -TB02 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | GAS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF07 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 15 | =G01NHY01KF001-TB02&EFS.001 |  |  |  | U012UNA01UH100
=K01CCA01UH001 | K01CCA01UH001-BA22 | =K01CCA01UH001-BA22;XU01 | CTRL AUTOM CAB1 230VAC GRP FLT GRP FLT | 38 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 AUTOMATION SYSTEM AUTOMATION SYSTEM AUTOMATION CABINET AUTOMATION CABINET GROUP FAULT ALARM 230V GROUP FAULT ALARM | =K | Plant Control System | 01 | Plant Control System 1 | CCA | Automation System | 01 | Automation System | UH | Automation Cabinet | 001 | Automation Cabinet | -BA22 | Group Fault Alarm 230V | XU01 | Group fault alarm | CTRL | Autom | Cab1 | 230VAC GRP FLT | GRP FLT | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | E | [15 empty] | =K01CCA01UH001+U012UBB01UH001-DIa | DIa, 6 digital inputs (1p) | B10:XU01 | EA01 | 01 | =K01CCA01UH001-BA22&EFS.001 |  |  |  | U012UBB01UH001
=K01CCA01UH001 | K01CCA01UH001-BA41 | =K01CCA01UH001-BA41;XU01 | CTRL AUTOM CAB1 UPS MON GRP FLT | 31 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 AUTOMATION SYSTEM AUTOMATION SYSTEM AUTOMATION CABINET AUTOMATION CABINET GROUP FAULT ALARM 230V UPS GROUP FAULT ALARM | =K | Plant Control System | 01 | Plant Control System 1 | CCA | Automation System | 01 | Automation System | UH | Automation Cabinet | 001 | Automation Cabinet | -BA41 | Group Fault Alarm 230V UPS | XU01 | Group fault alarm | CTRL | Autom | Cab1 | UPS MON | GRP FLT | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | E | [15 empty] | =K01CCA01UH001+U012UBB01UH001-DIa | DIa, 6 digital inputs (1p) | B10:XU01 | EA01 | 02 | =K01CCA01UH001-BA41&EFS.001 |  |  |  | U012UBB01UH001
=K01CCA01UH001 | K01CCA01UH001-FC01 | =K01CCA01UH001-FC01;XU01 | CTRL AUTOM CAB1 24V MON1 GRP FLT | 32 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 AUTOMATION SYSTEM AUTOMATION SYSTEM AUTOMATION CABINET AUTOMATION CABINET GROUP FAULT ALARM 24VDC SELECTIVITY MODULE GROUP FAULT ALARM | =K | Plant Control System | 01 | Plant Control System 1 | CCA | Automation System | 01 | Automation System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC01 | Group Fault Alarm 24VDC Selectivity module | XU01 | Group fault alarm | CTRL | Autom | Cab1 | 24V MON1 | GRP FLT | -FC03 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | E | [15 empty] | =K01CCA01UH001+U012UBB01UH001-DIa | DIa, 6 digital inputs (1p) | B10:XU01 | EA01 | 03 | =K01CCA01UH001-FC01&EFS.001 |  |  |  | U012UBB01UH001
=K01CCA01UH001 | K01CCA01UH001-TB01 | =K01CCA01UH001-TB01;XU01 | CTRL AUTOM CAB1 24VDC MON1 GRP FLT | 34 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 AUTOMATION SYSTEM AUTOMATION SYSTEM AUTOMATION CABINET AUTOMATION CABINET GROUP FAULT ALARM 24VDC UPS GENERATION GROUP FAULT ALARM | =K | Plant Control System | 01 | Plant Control System 1 | CCA | Automation System | 01 | Automation System | UH | Automation Cabinet | 001 | Automation Cabinet | -TB01 | Group Fault Alarm 24VDC UPS Generation | XU01 | Group fault alarm | CTRL | Autom | Cab1 | 24VDC MON1 | GRP FLT | -TB02 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | E | [15 empty] | =K01CCA01UH001+U012UBB01UH001-DIa | DIa, 6 digital inputs (1p) | B10:XU01 | EA01 | 04 | =K01CCA01UH001-TB01&EFS.001 |  |  |  | U012UBB01UH001
=K01CCA01UH001 | K01CCA01UH001-TF01 | =K01CCA01UH001-TF01;XU01 | CTRL AUTOM CAB1 DC MON1 GRP FLT | 31 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 AUTOMATION SYSTEM AUTOMATION SYSTEM AUTOMATION CABINET AUTOMATION CABINET GROUP FAULT ALARM LAN GROUP FAULT ALARM | =K | Plant Control System | 01 | Plant Control System 1 | CCA | Automation System | 01 | Automation System | UH | Automation Cabinet | 001 | Automation Cabinet | -TF01 | Group Fault Alarm LAN | XU01 | Group fault alarm | CTRL | Autom | Cab1 | DC MON1 | GRP FLT |  | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | E | [15 empty] | =K01CCA01UH001+U012UBB01UH001-DIa | DIa, 6 digital inputs (1p) | B10:XU01 | EA01 | 05 | =K01CCA01UH001-TF01&EFS.001 |  |  |  | U012UBB01UH001
=K01CSY01UH001 | K01CSY01UH001-BA11 | =K01CSY01UH001-BA11;XB01 | CTRL PLNT CAB1 400VAC MON CB ON/OPN | 35 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 400VAC MONITORING CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -BA11 | 400VAC Monitoring | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 400VAC MON | CB ON/OPN | 1 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 02 | =K01CSY01UH001-BA11&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-BA21 | =K01CSY01UH001-BA21;XB01 | CTRL PLNT CAB1 230VAC MON CB ON/OPN | 35 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 2300VAC MONITORING CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -BA21 | 2300VAC Monitoring | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC MON | CB ON/OPN | 1 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 08 | =K01CSY01UH001-BA21&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-BA41 | =K01CSY01UH001-BA41;XB01 | CTRL PLNT CAB1 UPS MON CB ON/OPN | 32 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC UPS MONITORING CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -BA41 | 230VAC UPS Monitoring | XB01 | Check back on/open | CTRL | PLNT | Cab1 | UPS MON | CB ON/OPN | 1 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 13 | =K01CSY01UH001-BA41&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC01 | =K01CSY01UH001-FC01;XB01 | CTRL PLNT CAB1 24V MON1 CB ON/OPN | 33 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 24VDC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC01 | 24VDC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 24V MON1 | CB ON/OPN | -FC01 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 04 | =K01CSY01UH001-FC01&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC02 | =K01CSY01UH001-FC02;XB01 | CTRL PLNT CAB1 24V MON2 CB ON/OPN | 33 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 24VDC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC02 | 24VDC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 24V MON2 | CB ON/OPN | -FC02 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 05 | =K01CSY01UH001-FC02&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC03 | =K01CSY01UH001-FC03;XB01 | CTRL PLNT CAB1 24V MON3 CB ON/OPN | 33 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 24VDC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC03 | 24VDC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 24V MON3 | CB ON/OPN | -FC03 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 06 | =K01CSY01UH001-FC03&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC11 | =K01CSY01UH001-FC11;XB01 | CTRL PLNT CAB1 400VAC IN CB ON/OPN | 34 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 400VAC INPUT CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC11 | 400VAC Input | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 400VAC In | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 01 | =K01CSY01UH001-FC11&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC21 | =K01CSY01UH001-FC21;XB01 | CTRL PLNT CAB1 230VAC1 CB ON/OPN | 32 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC21 | 230VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC1 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 07 | =K01CSY01UH001-FC21&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC22 | =K01CSY01UH001-FC22;XB01 | CTRL PLNT CAB1 230VAC2 CB ON/OPN | 32 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC22 | 230VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC2 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 09 | =K01CSY01UH001-FC22&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC23 | =K01CSY01UH001-FC23;XB01 | CTRL PLNT CAB1 230VAC3 CB ON/OPN | 32 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC23 | 230VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC3 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 10 | =K01CSY01UH001-FC23&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC24 | =K01CSY01UH001-FC24;XB01 | CTRL PLNT CAB1 230VAC4 CB ON/OPN | 32 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC24 | 230VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC4 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 11 | =K01CSY01UH001-FC24&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC25 | =K01CSY01UH001-FC25;XB01 | CTRL PLNT CAB1 230VAC5 CB ON/OPN | 32 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC25 | 230VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC5 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 12 | =K01CSY01UH001-FC25&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC26 | =K01CSY01UH001-FC26;XB01 | CTRL PLNT CAB1 230VAC6 CB ON/OPN | 32 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC26 | 230VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC6 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 13 | =K01CSY01UH001-FC26&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC27 | =K01CSY01UH001-FC27;XB01 | CTRL PLNT CAB1 230VAC7 CB ON/OPN | 32 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC27 | 230VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC7 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 14 | =K01CSY01UH001-FC27&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC28 | =K01CSY01UH001-FC28;XB01 | CTRL PLNT CAB1 230VAC8 CB ON/OPN | 32 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC28 | 230VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC8 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 15 | =K01CSY01UH001-FC28&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC29 | =K01CSY01UH001-FC29;XB01 | CTRL PLNT CAB1 230VAC9 CB ON/OPN | 32 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC29 | 230VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC9 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 16 | =K01CSY01UH001-FC29&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC30 | =K01CSY01UH001-FC30;XB01 | CTRL PLNT CAB1 230VAC10 CB ON/OPN | 33 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC30 | 230VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC10 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 01 | =K01CSY01UH001-FC30&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC31 | =K01CSY01UH001-FC31;XB01 | CTRL PLNT CAB1 230VAC11 CB ON/OPN | 33 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC31 | 230VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC11 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 02 | =K01CSY01UH001-FC31&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC32 | =K01CSY01UH001-FC32;XB01 | CTRL PLNT CAB1 230VAC12 CB ON/OPN | 33 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC32 | 230VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC12 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 03 | =K01CSY01UH001-FC32&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC33 | =K01CSY01UH001-FC33;XB01 | CTRL PLNT CAB1 230VAC13 CB ON/OPN | 33 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC33 | 230VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC13 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 04 | =K01CSY01UH001-FC33&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC34 | =K01CSY01UH001-FC34;XB01 | CTRL PLNT CAB1 230VAC14 CB ON/OPN | 33 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC34 | 230VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC14 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 05 | =K01CSY01UH001-FC34&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC35 | =K01CSY01UH001-FC35;XB01 | CTRL PLNT CAB1 230VAC15 CB ON/OPN | 33 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC35 | 230VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC15 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 06 | =K01CSY01UH001-FC35&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC36 | =K01CSY01UH001-FC36;XB01 | CTRL PLNT CAB1 230VAC16 CB ON/OPN | 33 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC36 | 230VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC16 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 07 | =K01CSY01UH001-FC36&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC37 | =K01CSY01UH001-FC37;XB01 | CTRL PLNT CAB1 230VAC17 CB ON/OPN | 33 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC37 | 230VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC17 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 08 | =K01CSY01UH001-FC37&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC38 | =K01CSY01UH001-FC38;XB01 | CTRL PLNT CAB1 230VAC18 CB ON/OPN | 33 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC38 | 230VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC18 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 09 | =K01CSY01UH001-FC38&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC39 | =K01CSY01UH001-FC39;XB01 | CTRL PLNT CAB1 230VAC19 CB ON/OPN | 33 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC39 | 230VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC19 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 10 | =K01CSY01UH001-FC39&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC40 | =K01CSY01UH001-FC40;XB01 | CTRL PLNT CAB1 230VAC20 CB ON/OPN | 33 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC40 | 230VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC20 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 11 | =K01CSY01UH001-FC40&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC41 | =K01CSY01UH001-FC41;XB01 | CTRL PLNT CAB1 230VAC UPS1 CB ON/OPN | 36 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC41 | 230VAC UPS Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC UPS1 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 12 | =K01CSY01UH001-FC41&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC42 | =K01CSY01UH001-FC42;XB01 | CTRL PLNT CAB1 230VAC UPS2 CB ON/OPN | 36 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC42 | 230VAC UPS Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC UPS2 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 14 | =K01CSY01UH001-FC42&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC43 | =K01CSY01UH001-FC43;XB01 | CTRL PLNT CAB1 230VAC UPS3 CB ON/OPN | 36 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC43 | 230VAC UPS Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC UPS3 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 15 | =K01CSY01UH001-FC43&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC44 | =K01CSY01UH001-FC44;XB01 | CTRL PLNT CAB1 230VAC UPS4 CB ON/OPN | 36 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC44 | 230VAC UPS Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC UPS4 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF02 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 16 | =K01CSY01UH001-FC44&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-FC45 | =K01CSY01UH001-FC45;XB01 | CTRL PLNT CAB1 230VAC UPS5 CB ON/OPN | 36 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 230VAC UPS DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -FC45 | 230VAC UPS Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 230VAC UPS5 | CB ON/OPN | SF011 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 01 | =K01CSY01UH001-FC45&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-QA11 | =K01CSY01UH001-QA11;XB01 | CTRL PLNT CAB1 SW 400VAC1 CB ON/OPN | 35 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -QA11 | 400VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | Sw 400VAC1 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 03 | =K01CSY01UH001-QA11&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-QA12 | =K01CSY01UH001-QA12;XB01 | CTRL PLNT CAB1 SW 400VAC2 CB ON/OPN | 35 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -QA12 | 400VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | Sw 400VAC2 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 04 | =K01CSY01UH001-QA12&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-QA13 | =K01CSY01UH001-QA13;XB01 | CTRL PLNT CAB1 SW 400VAC3 CB ON/OPN | 35 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -QA13 | 400VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | Sw 400VAC3 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 05 | =K01CSY01UH001-QA13&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-QA14 | =K01CSY01UH001-QA14;XB01 | CTRL PLNT CAB1 SW 400VAC4 CB ON/OPN | 35 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET 400VAC DISTRIBUTION CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -QA14 | 400VAC Distribution | XB01 | Check back on/open | CTRL | PLNT | Cab1 | Sw 400VAC4 | CB ON/OPN | 2 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF01 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 06 | =K01CSY01UH001-QA14&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-SF01 | =K01CSY01UH001-SF01;XW02 | CTRL PLNT CAB1 SW OFF WARN CODE | 31 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET EMERGENCY STOP - PUSHBUTTON - CABINET I&C ELECTROLYSIS ARRAY COMPONENT PROTECTION | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -SF01 | Emergency Stop - Pushbutton - Cabinet I&C Electrolysis Array | XW02 | Component protection | CTRL | PLNT | Cab1 | Sw OFF | WARN CODE |  | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 |  |  | B10:XW02 | XW02 |  | =K01CSY01UH001-SF01&EFS.001
=K01CSY01UH001 | K01CSY01UH001-SF01 | =K01CSY01UH001-SF01;XW01 | CTRL PLNT CAB1 SW OFF AL/FLT CODE | 33 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET EMERGENCY STOP - PUSHBUTTON - CABINET I&C ELECTROLYSIS ARRAY COMPONENT PROTECTION | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -SF01 | Emergency Stop - Pushbutton - Cabinet I&C Electrolysis Array | XW01 | Component protection | CTRL | PLNT | Cab1 | Sw OFF | AL/FLT CODE |  | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 |  |  | B10:XW01 | XW01 |  | =K01CSY01UH001-SF01&EFS.001
=K01CSY01UH001 | K01CSY01UH001-TB01 | =K01CSY01UH001-TB01;XB01 | CTRL PLNT CAB1 24VDC MON1 CB ON/OPN | 35 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET SITOP PSU6200 24 V/20 A CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -TB01 | SITOP PSU6200 24 V/20 A | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 24VDC MON1 | CB ON/OPN | -TB01 | Electrical | 24 VDC | 24 VDC | Wire | Continuous signal |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 02 | =K01CSY01UH001-TB01&EFS.001 |  |  |  | U012UBB01UH002
=K01CSY01UH001 | K01CSY01UH001-TB02 | =K01CSY01UH001-TB02;XB01 | CTRL PLNT CAB1 24VDC MON2 CB ON/OPN | 35 | PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM 1 PLANT CONTROL SYSTEM PLANT CONTROL SYSTEM AUTOMATION CABINET AUTOMATION CABINET SITOP PSU6200 24 V/20 A CHECK BACK ON/OPEN | =K | Plant Control System | 01 | Plant Control System 1 | CSY | Plant Control System | 01 | Plant Control System | UH | Automation Cabinet | 001 | Automation Cabinet | -TB02 | SITOP PSU6200 24 V/20 A | XB01 | Check back on/open | CTRL | PLNT | Cab1 | 24VDC MON2 | CB ON/OPN | -TB02 | Electrical | 24 VDC | 24 VDC | Wire | Pulsed |  |  | DI | 0 | G | [15 empty] | =K01CSY01UH001+U012UBB01UH002-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 03 | =K01CSY01UH001-TB02&EFS.001 |  |  |  | U012UBB01UH002
=T01BBA01QA001 | T01BBA01QA001-QA01 | =T01BBA01QA001-QA01;XJ01 | EL POW SUP MV MV DIST1 SW1 RDY F OP | 35 | ELECTRICAL POWER SUPPLY SYSTEM SYSTEM 1 MV SUPPLY SYSTEM - 20KV SYSTEM 1 MV DISTRIBUTION MV DISTRIBUTION UNIT - ARRAY 1 POWER CIRCUIT-BREAKER, 3-POLE READY TO SWITCH ON | =T | Electrical Power Supply System | 01 | System 1 | BBA | MV Supply System - 20kV | 01 | System 1 | QA | MV Distribution | 001 | MV Distribution Unit - Array 1 | -QA01 | Power circuit-breaker, 3-pole | XJ01 | Ready to switch on | El Pow Sup | MV | MV DIST1 | Sw1 | RDY F OP | -XG10 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DI | 0 | GH | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XJ01 | EA01 | 10 | =T01BBA01QA001-QA01&EFS.002 |  |  |  | U012UBB01UC001
=T01BBA01QA001 | T01BBA01QA001-QA01 | =T01BBA01QA001-QA01;XB01 | EL POW SUP MV MV DIST1 SW1 CB ON/OPN | 36 | ELECTRICAL POWER SUPPLY SYSTEM SYSTEM 1 MV SUPPLY SYSTEM - 20KV SYSTEM 1 MV DISTRIBUTION MV DISTRIBUTION UNIT - ARRAY 1 POWER CIRCUIT-BREAKER, 3-POLE CHECK BACK ON/OPEN | =T | Electrical Power Supply System | 01 | System 1 | BBA | MV Supply System - 20kV | 01 | System 1 | QA | MV Distribution | 001 | MV Distribution Unit - Array 1 | -QA01 | Power circuit-breaker, 3-pole | XB01 | Check back on/open | El Pow Sup | MV | MV DIST1 | Sw1 | CB ON/OPN | -XG10 | Electrical |  |  | Wire | Undefined |  |  | DI | 0 | GH | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | EA01 | 08 | =T01BBA01QA001-QA01&EFS.002 |  |  |  | U012UBB01UC001
=T01BBA01QA001 | T01BBA01QA001-QA01 | =T01BBA01QA001-QA01;XB02 | EL POW SUP MV MV DIST1 SW1 CB OFF/CLD | 37 | ELECTRICAL POWER SUPPLY SYSTEM SYSTEM 1 MV SUPPLY SYSTEM - 20KV SYSTEM 1 MV DISTRIBUTION MV DISTRIBUTION UNIT - ARRAY 1 POWER CIRCUIT-BREAKER, 3-POLE CHECK BACK OFF/CLOSED | =T | Electrical Power Supply System | 01 | System 1 | BBA | MV Supply System - 20kV | 01 | System 1 | QA | MV Distribution | 001 | MV Distribution Unit - Array 1 | -QA01 | Power circuit-breaker, 3-pole | XB02 | Check back off/closed | El Pow Sup | MV | MV DIST1 | Sw1 | CB OFF/CLD | -XG10 | Electrical |  |  | Wire | Undefined |  |  | DI | 0 | GH | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF05 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB02 | EA01 | 09 | =T01BBA01QA001-QA01&EFS.002 |  |  |  | U012UBB01UC001
=V01NHC20CM001 | V01NHC20CM001-BL04 | =V01NHC20CM001-BL04;XH01 | GAS TRT H2 LP BUF TNK1 LVL4 AL MAX 1 | 36 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 BUFFER TANK BUFFER TANK SYSTEMS BUFFER TANK SYSTEM 10761; VIBR. LEVEL DET., COMP. SYST. LIMIT VALUE >MAX 1 | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 20 | H2 Buffer Tank | CM | Buffer Tank Systems | 001 | Buffer Tank System | -BL04 | 10761; Vibr. level det., comp. syst. | XH01 | Limit value >max 1 | Gas TRT | H2 LP Buf | Tnk1 | Lvl4 | AL MAX 1 | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | LI | [21 empty] | =V01NHC20&MFB.001
=V01NHC20CM001 | V01NHC20CM001-BL05 | =V01NHC20CM001-BL05;XH01 | GAS TRT H2 LP BUF TNK1 LVL5 AL MAX 1 | 36 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 BUFFER TANK BUFFER TANK SYSTEMS BUFFER TANK SYSTEM 10761; VIBR. LEVEL DET., COMP. SYST. LIMIT VALUE >MAX 1 | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 20 | H2 Buffer Tank | CM | Buffer Tank Systems | 001 | Buffer Tank System | -BL05 | 10761; Vibr. level det., comp. syst. | XH01 | Limit value >max 1 | Gas TRT | H2 LP Buf | Tnk1 | Lvl5 | AL MAX 1 | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DI | 0 | LI | [7 empty] | AH | [13 empty] | =V01NHC20&MFB.001
=V01NHC30WP001 | V01NHC30WP001-QM02 | =V01NHC30WP001-QM02;XB01 | GAS TRT H2 COMPR PIPING SV2 CB ON/OPN | 37 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 30BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM INLET LINE 2-WAY SHUT-OFF VALVE (GENERAL) CHECK BACK ON/OPEN | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 30 | H2 Compressor System 30bar | WP | Compressor Pipe Systems | 001 | Compressor Pipe System Inlet Line | -QM02 | 2-way shut-off valve (general) | XB01 | Check back on/open | Gas TRT | H2 Compr | Piping | SV2 | CB ON/OPN | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC30&MFB.001
=V01NHC30WP001 | V01NHC30WP001-QM02 | =V01NHC30WP001-QM02;XB02 | GAS TRT H2 COMPR PIPING SV2 CB OFF/CLD | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 30BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM INLET LINE 2-WAY SHUT-OFF VALVE (GENERAL) CHECK BACK OFF/CLOSED | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 30 | H2 Compressor System 30bar | WP | Compressor Pipe Systems | 001 | Compressor Pipe System Inlet Line | -QM02 | 2-way shut-off valve (general) | XB02 | Check back off/closed | Gas TRT | H2 Compr | Piping | SV2 | CB OFF/CLD | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC30&MFB.001
=V01NHC30WP001 | V01NHC30WP001-QM03 | =V01NHC30WP001-QM03;XB01 | GAS TRT H2 COMPR PIPING SV3 CB ON/OPN | 37 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 30BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM INLET LINE BALL VALVE (GENERAL) CHECK BACK ON/OPEN | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 30 | H2 Compressor System 30bar | WP | Compressor Pipe Systems | 001 | Compressor Pipe System Inlet Line | -QM03 | Ball valve (general) | XB01 | Check back on/open | Gas TRT | H2 Compr | Piping | SV3 | CB ON/OPN | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC30&MFB.001
=V01NHC30WP001 | V01NHC30WP001-QM03 | =V01NHC30WP001-QM03;XB02 | GAS TRT H2 COMPR PIPING SV3 CB OFF/CLD | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 30BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM INLET LINE BALL VALVE (GENERAL) CHECK BACK OFF/CLOSED | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 30 | H2 Compressor System 30bar | WP | Compressor Pipe Systems | 001 | Compressor Pipe System Inlet Line | -QM03 | Ball valve (general) | XB02 | Check back off/closed | Gas TRT | H2 Compr | Piping | SV3 | CB OFF/CLD | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC30&MFB.001
=V01NHC30WP001 | V01NHC30WP001-QM06 | =V01NHC30WP001-QM06;XB01 | GAS TRT H2 COMPR PIPING SV6 CB ON/OPN | 37 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 30BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM INLET LINE BUTTERFLY VALVE (GEN.) CHECK BACK ON/OPEN | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 30 | H2 Compressor System 30bar | WP | Compressor Pipe Systems | 001 | Compressor Pipe System Inlet Line | -QM06 | Butterfly valve (gen.) | XB01 | Check back on/open | Gas TRT | H2 Compr | Piping | SV6 | CB ON/OPN | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC30&MFB.001
=V01NHC30WP001 | V01NHC30WP001-QM06 | =V01NHC30WP001-QM06;XB02 | GAS TRT H2 COMPR PIPING SV6 CB OFF/CLD | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 30BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM INLET LINE BUTTERFLY VALVE (GEN.) CHECK BACK OFF/CLOSED | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 30 | H2 Compressor System 30bar | WP | Compressor Pipe Systems | 001 | Compressor Pipe System Inlet Line | -QM06 | Butterfly valve (gen.) | XB02 | Check back off/closed | Gas TRT | H2 Compr | Piping | SV6 | CB OFF/CLD | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC30&MFB.001
=V01NHC30WP002 | V01NHC30WP002-QM01 | =V01NHC30WP002-QM01;XB01 | GAS TRT H2 COMPR PIPING SV1 CB ON/OPN | 37 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 30BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM OUTLET LINE BALL VALVE (GENERAL) CHECK BACK ON/OPEN | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 30 | H2 Compressor System 30bar | WP | Compressor Pipe Systems | 002 | Compressor Pipe System Outlet Line | -QM01 | Ball valve (general) | XB01 | Check back on/open | Gas TRT | H2 Compr | Piping | SV1 | CB ON/OPN | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC30&MFB.001
=V01NHC30WP002 | V01NHC30WP002-QM01 | =V01NHC30WP002-QM01;XB02 | GAS TRT H2 COMPR PIPING SV1 CB OFF/CLD | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 30BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM OUTLET LINE BALL VALVE (GENERAL) CHECK BACK OFF/CLOSED | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 30 | H2 Compressor System 30bar | WP | Compressor Pipe Systems | 002 | Compressor Pipe System Outlet Line | -QM01 | Ball valve (general) | XB02 | Check back off/closed | Gas TRT | H2 Compr | Piping | SV1 | CB OFF/CLD | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC30&MFB.001
=V01NHC31WP001 | V01NHC31WP001-QM01 | =V01NHC31WP001-QM01;XB01 | GAS TRT H2 COMPR PIPING SV1 CB ON/OPN | 37 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 100BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM INLET LINE BUTTERFLY VALVE (GEN.) CHECK BACK ON/OPEN | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 31 | H2 Compressor System 100bar | WP | Compressor Pipe Systems | 001 | Compressor Pipe System Inlet Line | -QM01 | Butterfly valve (gen.) | XB01 | Check back on/open | Gas TRT | H2 Compr | Piping | SV1 | CB ON/OPN | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC31&MFB.001
=V01NHC31WP001 | V01NHC31WP001-QM01 | =V01NHC31WP001-QM01;XB02 | GAS TRT H2 COMPR PIPING SV1 CB OFF/CLD | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 100BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM INLET LINE BUTTERFLY VALVE (GEN.) CHECK BACK OFF/CLOSED | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 31 | H2 Compressor System 100bar | WP | Compressor Pipe Systems | 001 | Compressor Pipe System Inlet Line | -QM01 | Butterfly valve (gen.) | XB02 | Check back off/closed | Gas TRT | H2 Compr | Piping | SV1 | CB OFF/CLD | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC31&MFB.001
=V01NHC31WP001 | V01NHC31WP001-QM02 | =V01NHC31WP001-QM02;XB01 | GAS TRT H2 COMPR PIPING SV2 CB ON/OPN | 37 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 100BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM INLET LINE 2-WAY SHUT-OFF VALVE (GENERAL) CHECK BACK ON/OPEN | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 31 | H2 Compressor System 100bar | WP | Compressor Pipe Systems | 001 | Compressor Pipe System Inlet Line | -QM02 | 2-way shut-off valve (general) | XB01 | Check back on/open | Gas TRT | H2 Compr | Piping | SV2 | CB ON/OPN | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC31&MFB.001
=V01NHC31WP001 | V01NHC31WP001-QM02 | =V01NHC31WP001-QM02;XB02 | GAS TRT H2 COMPR PIPING SV2 CB OFF/CLD | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 100BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM INLET LINE 2-WAY SHUT-OFF VALVE (GENERAL) CHECK BACK OFF/CLOSED | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 31 | H2 Compressor System 100bar | WP | Compressor Pipe Systems | 001 | Compressor Pipe System Inlet Line | -QM02 | 2-way shut-off valve (general) | XB02 | Check back off/closed | Gas TRT | H2 Compr | Piping | SV2 | CB OFF/CLD | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC31&MFB.001
=V01NHC31WP001 | V01NHC31WP001-QM03 | =V01NHC31WP001-QM03;XB01 | GAS TRT H2 COMPR PIPING SV3 CB ON/OPN | 37 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 100BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM INLET LINE BALL VALVE (GENERAL) CHECK BACK ON/OPEN | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 31 | H2 Compressor System 100bar | WP | Compressor Pipe Systems | 001 | Compressor Pipe System Inlet Line | -QM03 | Ball valve (general) | XB01 | Check back on/open | Gas TRT | H2 Compr | Piping | SV3 | CB ON/OPN | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC31&MFB.001
=V01NHC31WP001 | V01NHC31WP001-QM03 | =V01NHC31WP001-QM03;XB02 | GAS TRT H2 COMPR PIPING SV3 CB OFF/CLD | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 100BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM INLET LINE BALL VALVE (GENERAL) CHECK BACK OFF/CLOSED | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 31 | H2 Compressor System 100bar | WP | Compressor Pipe Systems | 001 | Compressor Pipe System Inlet Line | -QM03 | Ball valve (general) | XB02 | Check back off/closed | Gas TRT | H2 Compr | Piping | SV3 | CB OFF/CLD | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC31&MFB.001
=V01NHC60BZ001 | V01NHC60BZ001-QM01 | =V01NHC60BZ001-QM01;XB01 | GAS TRT H2 HANDOVR MEAS1 SV1 CB ON/OPN | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIC SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 BALL VALVE (GENERAL) CHECK BACK ON/OPEN | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 60 | Product Gas Analytic System | BZ | Measurement Systems | 001 | Measurement System 1 | -QM01 | Ball valve (general) | XB01 | Check back on/open | Gas TRT | H2 Handovr | Meas1 | SV1 | CB ON/OPN | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC60&MFB.001
=V01NHC60BZ001 | V01NHC60BZ001-QM01 | =V01NHC60BZ001-QM01;XB02 | GAS TRT H2 HANDOVR MEAS1 SV1 CB OFF/CLD | 39 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIC SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 BALL VALVE (GENERAL) CHECK BACK OFF/CLOSED | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 60 | Product Gas Analytic System | BZ | Measurement Systems | 001 | Measurement System 1 | -QM01 | Ball valve (general) | XB02 | Check back off/closed | Gas TRT | H2 Handovr | Meas1 | SV1 | CB OFF/CLD | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC60&MFB.001
=V01NHC60BZ001 | V01NHC60BZ001-QM02 | =V01NHC60BZ001-QM02;XB01 | GAS TRT H2 HANDOVR MEAS1 SV2 CB ON/OPN | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIC SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 BALL VALVE (GENERAL) CHECK BACK ON/OPEN | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 60 | Product Gas Analytic System | BZ | Measurement Systems | 001 | Measurement System 1 | -QM02 | Ball valve (general) | XB01 | Check back on/open | Gas TRT | H2 Handovr | Meas1 | SV2 | CB ON/OPN | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC60&MFB.001
=V01NHC60BZ001 | V01NHC60BZ001-QM02 | =V01NHC60BZ001-QM02;XB02 | GAS TRT H2 HANDOVR MEAS1 SV2 CB OFF/CLD | 39 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIC SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 BALL VALVE (GENERAL) CHECK BACK OFF/CLOSED | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 60 | Product Gas Analytic System | BZ | Measurement Systems | 001 | Measurement System 1 | -QM02 | Ball valve (general) | XB02 | Check back off/closed | Gas TRT | H2 Handovr | Meas1 | SV2 | CB OFF/CLD | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC60&MFB.001
=V01NHC60BZ001 | V01NHC60BZ001-QM03 | =V01NHC60BZ001-QM03;XB01 | GAS TRT H2 HANDOVR MEAS1 SV3 CB ON/OPN | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIC SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 BALL VALVE (GENERAL) CHECK BACK ON/OPEN | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 60 | Product Gas Analytic System | BZ | Measurement Systems | 001 | Measurement System 1 | -QM03 | Ball valve (general) | XB01 | Check back on/open | Gas TRT | H2 Handovr | Meas1 | SV3 | CB ON/OPN | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC60&MFB.001
=V01NHC60BZ001 | V01NHC60BZ001-QM03 | =V01NHC60BZ001-QM03;XB02 | GAS TRT H2 HANDOVR MEAS1 SV3 CB OFF/CLD | 39 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIC SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 BALL VALVE (GENERAL) CHECK BACK OFF/CLOSED | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 60 | Product Gas Analytic System | BZ | Measurement Systems | 001 | Measurement System 1 | -QM03 | Ball valve (general) | XB02 | Check back off/closed | Gas TRT | H2 Handovr | Meas1 | SV3 | CB OFF/CLD | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC60&MFB.001
=V01NHC61BZ001 | V01NHC61BZ001-QM01 | =V01NHC61BZ001-QM01;XB01 | GAS TRT H2 HANDOVR MEAS1 SV1 CB ON/OPN | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIK SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 BALL VALVE (GENERAL) CHECK BACK ON/OPEN | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 61 | Product Gas Analytik System | BZ | Measurement Systems | 001 | Measurement System 1 | -QM01 | Ball valve (general) | XB01 | Check back on/open | Gas TRT | H2 Handovr | Meas1 | SV1 | CB ON/OPN | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC61&MFB.001
=V01NHC61BZ001 | V01NHC61BZ001-QM01 | =V01NHC61BZ001-QM01;XB02 | GAS TRT H2 HANDOVR MEAS1 SV1 CB OFF/CLD | 39 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIK SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 BALL VALVE (GENERAL) CHECK BACK OFF/CLOSED | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 61 | Product Gas Analytik System | BZ | Measurement Systems | 001 | Measurement System 1 | -QM01 | Ball valve (general) | XB02 | Check back off/closed | Gas TRT | H2 Handovr | Meas1 | SV1 | CB OFF/CLD | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC61&MFB.001
=V01NHC61BZ001 | V01NHC61BZ001-QM02 | =V01NHC61BZ001-QM02;XB01 | GAS TRT H2 HANDOVR MEAS1 SV2 CB ON/OPN | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIK SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 BALL VALVE (GENERAL) CHECK BACK ON/OPEN | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 61 | Product Gas Analytik System | BZ | Measurement Systems | 001 | Measurement System 1 | -QM02 | Ball valve (general) | XB01 | Check back on/open | Gas TRT | H2 Handovr | Meas1 | SV2 | CB ON/OPN | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC61&MFB.001
=V01NHC61BZ001 | V01NHC61BZ001-QM02 | =V01NHC61BZ001-QM02;XB02 | GAS TRT H2 HANDOVR MEAS1 SV2 CB OFF/CLD | 39 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIK SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 BALL VALVE (GENERAL) CHECK BACK OFF/CLOSED | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 61 | Product Gas Analytik System | BZ | Measurement Systems | 001 | Measurement System 1 | -QM02 | Ball valve (general) | XB02 | Check back off/closed | Gas TRT | H2 Handovr | Meas1 | SV2 | CB OFF/CLD | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC61&MFB.001
=V01NHC61BZ001 | V01NHC61BZ001-QM03 | =V01NHC61BZ001-QM03;XB01 | GAS TRT H2 HANDOVR MEAS1 SV3 CB ON/OPN | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIK SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 BALL VALVE (GENERAL) CHECK BACK ON/OPEN | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 61 | Product Gas Analytik System | BZ | Measurement Systems | 001 | Measurement System 1 | -QM03 | Ball valve (general) | XB01 | Check back on/open | Gas TRT | H2 Handovr | Meas1 | SV3 | CB ON/OPN | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC61&MFB.001
=V01NHC61BZ001 | V01NHC61BZ001-QM03 | =V01NHC61BZ001-QM03;XB02 | GAS TRT H2 HANDOVR MEAS1 SV3 CB OFF/CLD | 39 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIK SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 BALL VALVE (GENERAL) CHECK BACK OFF/CLOSED | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 61 | Product Gas Analytik System | BZ | Measurement Systems | 001 | Measurement System 1 | -QM03 | Ball valve (general) | XB02 | Check back off/closed | Gas TRT | H2 Handovr | Meas1 | SV3 | CB OFF/CLD | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 0 | G | [21 empty] | =V01NHC61&MFB.001
=A01GCF01GP001 | A01GCF01GP001-GP01 | =A01GCF01GP001-GP01;YB21 | AUX DEMIN SUP PMP1 PMP1 AUT CMD ON/OPN | 38 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS DEMIN WATER SUPPLY SYSTEM DEMIN WATER SUPPLY SYSTEM 1 PUMP SYSTEM PUMP SYSTEM 1 DEMIN WATER SUPPLY PUMP 1 AUTOMATIC COMMAND ON/OPEN | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | GCF | Demin Water Supply System | 01 | Demin Water Supply System 1 | GP | Pump System | 001 | Pump System 1 | -GP01 | Demin Water Supply Pump 1 | YB21 | Automatic command ON/OPEN | Aux | Demin Sup | PMP1 | PMP1 | AUT CMD ON/OPN | DR | Electrical | 24 VDC | 24 VDC | Field bus | Continuous signal |  |  | DO | 0 | NC | [21 empty] | =A01GCF01&MFB.001
=A01GCF01GP001 | A01GCF01GP001-GP02 | =A01GCF01GP001-GP02;YB21 | AUX DEMIN SUP PMP1 PMP2 AUT CMD ON/OPN | 38 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS DEMIN WATER SUPPLY SYSTEM DEMIN WATER SUPPLY SYSTEM 1 PUMP SYSTEM PUMP SYSTEM 1 DEMIN WATER SUPPLY PUMP 2 AUTOMATIC COMMAND ON/OPEN | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | GCF | Demin Water Supply System | 01 | Demin Water Supply System 1 | GP | Pump System | 001 | Pump System 1 | -GP02 | Demin Water Supply Pump 2 | YB21 | Automatic command ON/OPEN | Aux | Demin Sup | PMP1 | PMP2 | AUT CMD ON/OPN | DR | Electrical | 24 VDC | 24 VDC | Field bus | Continuous signal |  |  | DO | 0 | NC | [21 empty] | =A01GCF01&MFB.001
=A01PAD01GP001 | A01PAD01GP001-GP01 | =A01PAD01GP001-GP01;YB11 | AUX COOL WTR PMP1 PMP1 CMD ON/OP | 32 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING PUMP SYSTEM RECOOLING PUMP UNIT COOLING WATER RETURN PUMP 1 MANUAL COMMAND ON/OPEN | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | GP | Recooling Pump System | 001 | Recooling Pump Unit | -GP01 | Cooling Water Return Pump 1 | YB11 | Manual command ON/OPEN | Aux | Cool Wtr | PMP1 | PMP1 | CMD ON/OP |  | Electrical | 24 VDC | 24 VDC | Wire | Continuous signal |  |  | DO | 0 | NC | [21 empty] | =A01PAD01&MFB.001
=A01PAD01GP001 | A01PAD01GP001-GP02 | =A01PAD01GP001-GP02;YB11 | AUX COOL WTR PMP1 PMP2 CMD ON/OP | 32 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS COOLING WATER SYSTEMS COOLING WATER SYSTEM RECOOLING PUMP SYSTEM RECOOLING PUMP UNIT COOLING WATER RETURN PUMP 2 MANUAL COMMAND ON/OPEN | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | PAD | Cooling Water Systems | 01 | Cooling Water System | GP | Recooling Pump System | 001 | Recooling Pump Unit | -GP02 | Cooling Water Return Pump 2 | YB11 | Manual command ON/OPEN | Aux | Cool Wtr | PMP1 | PMP2 | CMD ON/OP |  | Electrical | 24 VDC | 24 VDC | Wire | Continuous signal |  |  | DO | 0 | NC | [21 empty] | =A01PAD01&MFB.001
=A01QJB01WP003 | A01QJB01WP003-QM11 | =A01QJB01WP003-QM11;YB11 | AUX N2 SUP PIPING SV11 CMD ON/OP | 32 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS NITROGEN SUPPLY SYSTEMS NITROGEN SUPPLY SYSTEM 1 PIPE SYSTEM NITROGEN SUPPLY AUX1 BALL VALVE (GENERAL) MANUAL COMMAND ON/OPEN | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | QJB | Nitrogen Supply Systems | 01 | Nitrogen Supply System 1 | WP | Pipe System | 003 | Nitrogen Supply AUX1 | -QM11 | Ball valve (general) | YB11 | Manual command ON/OPEN | Aux | N2 Sup | Piping | SV11 | CMD ON/OP | DR | Electrical | 24 VDC | 24 VDC | Wire | Continuous signal |  |  | DO | 0 | YS | [21 empty] | =V01NHC10&MFB.001
=A01QJB01WP003 | A01QJB01WP003-QM60 | =A01QJB01WP003-QM60;YB11 | AUX N2 SUP PIPING SV60 CMD ON/OP | 32 | ANCILLARY/AUXILIARY SYSTEMS AUXILLIARY SYSTEMS NITROGEN SUPPLY SYSTEMS NITROGEN SUPPLY SYSTEM 1 PIPE SYSTEM NITROGEN SUPPLY AUX1 BALL VALVE (GENERAL) MANUAL COMMAND ON/OPEN | =A | Ancillary/Auxiliary Systems | 01 | Auxilliary Systems | QJB | Nitrogen Supply Systems | 01 | Nitrogen Supply System 1 | WP | Pipe System | 003 | Nitrogen Supply AUX1 | -QM60 | Ball valve (general) | YB11 | Manual command ON/OPEN | Aux | N2 Sup | Piping | SV60 | CMD ON/OP | DR | Electrical | 24 VDC | 24 VDC | Wire | Continuous signal |  |  | DO | 0 | YS | [21 empty] | =A01QJB01&MFB.001
=G01NHA01EQ001 | G01NHA01EQ001-GP01 | =G01NHA01EQ001-GP01;YB11 | ELY1 RECT1 COOL PMP1 CMD ON/OP | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 COOLING SYSTEMS RECTIFIER COOLING SYSTEM PUMP, GENERAL MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | EQ | Cooling Systems | 001 | Rectifier Cooling System | -GP01 | Pump, general | YB11 | Manual command ON/OPEN | Ely1 | Rect1 | Cool | PMP1 | CMD ON/OP | -QA01 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 0 | NS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF06 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 01 | =G01NHA01EQ001-GP01&EFS.001 | =G01NHA01&MFB.001 |  |  | U012UBB01UC001
=G01NHA01EQ001 | G01NHA01EQ001-GP02 | =G01NHA01EQ001-GP02;YB11 | ELY1 RECT1 COOL PMP2 CMD ON/OP | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 COOLING SYSTEMS RECTIFIER COOLING SYSTEM PUMP, GENERAL MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | EQ | Cooling Systems | 001 | Rectifier Cooling System | -GP02 | Pump, general | YB11 | Manual command ON/OPEN | Ely1 | Rect1 | Cool | PMP2 | CMD ON/OP | -QA02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 0 | NS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF06 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 02 | =G01NHA01EQ001-GP02&EFS.002 | =G01NHA01&MFB.001 |  |  | U012UBB01UC001
=G01NHA01QZ001 | G01NHA01QZ001-QB01 | =G01NHA01QZ001-QB01;YB11 | ELY1 RECT1 DC SWG1 DISC DC+ CMD ON/OP | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 1 DISCONNECTOR - DC+ MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 001 | DC-Switchgear 1 | -QB01 | Disconnector - DC+ | YB11 | Manual command ON/OPEN | Ely1 | Rect1 | DC Swg1 | Disc DC+ | CMD ON/OP | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | NS | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF02 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | XG01:001 | 1 | 01 | =G01NHA01QZ001-QB01&EFS.003 |  |  |  | U012UBB01UC001
=G01NHA01QZ001 | G01NHA01QZ001-QB01 | =G01NHA01QZ001-QB01;YB12 | ELY1 RECT1 DC SWG1 DISC DC+ CMD OFF/CL | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 1 DISCONNECTOR - DC+ MANUAL COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 001 | DC-Switchgear 1 | -QB01 | Disconnector - DC+ | YB12 | Manual command OFF/CLOSE | Ely1 | Rect1 | DC Swg1 | Disc DC+ | CMD OFF/CL | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | NS | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF02 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | XG01:002 | 3 | 02 | =G01NHA01QZ001-QB01&EFS.003 |  |  |  | U012UBB01UC001
=G01NHA01QZ001 | G01NHA01QZ001-QB02 | =G01NHA01QZ001-QB02;YB11 | ELY1 RECT1 DC SWG1 DISC DC- CMD ON/OP | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 1 DISCONNECTOR - DC- MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 001 | DC-Switchgear 1 | -QB02 | Disconnector - DC- | YB11 | Manual command ON/OPEN | Ely1 | Rect1 | DC Swg1 | Disc DC- | CMD ON/OP | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | NS | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF02 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | B10:YB11 | YB11 | 03 | =G01NHA01QZ001-QB02&EFS.004 |  |  |  | U012UBB01UC001
=G01NHA01QZ001 | G01NHA01QZ001-QB02 | =G01NHA01QZ001-QB02;YB12 | ELY1 RECT1 DC SWG1 DISC DC- CMD OFF/CL | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 1 DISCONNECTOR - DC- MANUAL COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 001 | DC-Switchgear 1 | -QB02 | Disconnector - DC- | YB12 | Manual command OFF/CLOSE | Ely1 | Rect1 | DC Swg1 | Disc DC- | CMD OFF/CL | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | NS | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF02 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | B10:YB12 | YB12 | 04 | =G01NHA01QZ001-QB02&EFS.004 |  |  |  | U012UBB01UC001
=G01NHA01QZ002 | G01NHA01QZ002-QB01 | =G01NHA01QZ002-QB01;YB11 | ELY1 RECT1 DC SWG2 DISC DC+ CMD ON/OP | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 2 DISCONNECTOR - DC+ MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 002 | DC-Switchgear 2 | -QB01 | Disconnector - DC+ | YB11 | Manual command ON/OPEN | Ely1 | Rect1 | DC Swg2 | Disc DC+ | CMD ON/OP | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | NS | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF02 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | XG01:001 | 1 | 05 | =G01NHA01QZ002-QB01&EFS.003 |  |  |  | U012UBB01UC001
=G01NHA01QZ002 | G01NHA01QZ002-QB01 | =G01NHA01QZ002-QB01;YB12 | ELY1 RECT1 DC SWG2 DISC DC+ CMD OFF/CL | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 2 DISCONNECTOR - DC+ MANUAL COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 002 | DC-Switchgear 2 | -QB01 | Disconnector - DC+ | YB12 | Manual command OFF/CLOSE | Ely1 | Rect1 | DC Swg2 | Disc DC+ | CMD OFF/CL | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | NS | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF02 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | B10:YB12 | YB12 | 06 | =G01NHA01QZ002-QB01&EFS.003 |  |  |  | U012UBB01UC001
=G01NHA01QZ002 | G01NHA01QZ002-QB02 | =G01NHA01QZ002-QB02;YB11 | ELY1 RECT1 DC SWG2 DISC DC- CMD ON/OP | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 2 DISCONNECTOR - DC- MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 002 | DC-Switchgear 2 | -QB02 | Disconnector - DC- | YB11 | Manual command ON/OPEN | Ely1 | Rect1 | DC Swg2 | Disc DC- | CMD ON/OP | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | NS | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF02 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | B10:YB11 | YB11 | 07 | =G01NHA01QZ002-QB02&EFS.004 |  |  |  | U012UBB01UC001
=G01NHA01QZ002 | G01NHA01QZ002-QB02 | =G01NHA01QZ002-QB02;YB12 | ELY1 RECT1 DC SWG2 DISC DC- CMD OFF/CL | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 2 DISCONNECTOR - DC- MANUAL COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 002 | DC-Switchgear 2 | -QB02 | Disconnector - DC- | YB12 | Manual command OFF/CLOSE | Ely1 | Rect1 | DC Swg2 | Disc DC- | CMD OFF/CL | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | NS | [13 empty] | Yes |  | =G01NHA01KF001+U012UBB01UC001-KF02 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | B10:YB12 | YB12 | 08 | =G01NHA01QZ002-QB02&EFS.004 |  |  |  | U012UBB01UC001
=G01NHA01QZ003 | G01NHA01QZ003-QB01 | =G01NHA01QZ003-QB01;YB11 | ELY1 RECT1 DC SWG3 DISC DC+ CMD ON/OP | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 3 DISCONNECTOR - DC+ MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 003 | DC-Switchgear 3 | -QB01 | Disconnector - DC+ | YB11 | Manual command ON/OPEN | Ely1 | Rect1 | DC Swg3 | Disc DC+ | CMD ON/OP | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | NS | [13 empty] | Yes |  | =G01NHA01KF002+U012UBB01UC002-KF02 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | B10:YB11 | YB11B | 01 | =G01NHA01QZ003-QB01&EFS.003 |  |  |  | U012UBB01UC002
=G01NHA01QZ003 | G01NHA01QZ003-QB01 | =G01NHA01QZ003-QB01;YB12 | ELY1 RECT1 DC SWG3 DISC DC+ CMD OFF/CL | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 3 DISCONNECTOR - DC+ MANUAL COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 003 | DC-Switchgear 3 | -QB01 | Disconnector - DC+ | YB12 | Manual command OFF/CLOSE | Ely1 | Rect1 | DC Swg3 | Disc DC+ | CMD OFF/CL | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | NS | [13 empty] | Yes |  | =G01NHA01KF002+U012UBB01UC002-KF02 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | B10:YB12 | YB12 | 02 | =G01NHA01QZ003-QB01&EFS.003 |  |  |  | U012UBB01UC002
=G01NHA01QZ003 | G01NHA01QZ003-QB02 | =G01NHA01QZ003-QB02;YB11 | ELY1 RECT1 DC SWG3 DISC DC- CMD ON/OP | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 3 DISCONNECTOR - DC- MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 003 | DC-Switchgear 3 | -QB02 | Disconnector - DC- | YB11 | Manual command ON/OPEN | Ely1 | Rect1 | DC Swg3 | Disc DC- | CMD ON/OP | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | NS | [13 empty] | Yes |  | =G01NHA01KF002+U012UBB01UC002-KF02 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | B10:YB11 | YB11 | 03 | =G01NHA01QZ003-QB02&EFS.004 |  |  |  | U012UBB01UC002
=G01NHA01QZ003 | G01NHA01QZ003-QB02 | =G01NHA01QZ003-QB02;YB12 | ELY1 RECT1 DC SWG3 DISC DC- CMD OFF/CL | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 3 DISCONNECTOR - DC- MANUAL COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 003 | DC-Switchgear 3 | -QB02 | Disconnector - DC- | YB12 | Manual command OFF/CLOSE | Ely1 | Rect1 | DC Swg3 | Disc DC- | CMD OFF/CL | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | NS | [13 empty] | Yes |  | =G01NHA01KF002+U012UBB01UC002-KF02 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | B10:YB12 | YB12 | 04 | =G01NHA01QZ003-QB02&EFS.004 |  |  |  | U012UBB01UC002
=G01NHA01QZ004 | G01NHA01QZ004-QB01 | =G01NHA01QZ004-QB01;YB11 | ELY1 RECT1 DC SWG4 DISC DC+ CMD ON/OP | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 4 DISCONNECTOR - DC+ MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 004 | DC-Switchgear 4 | -QB01 | Disconnector - DC+ | YB11 | Manual command ON/OPEN | Ely1 | Rect1 | DC Swg4 | Disc DC+ | CMD ON/OP | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | NS | [13 empty] | Yes |  | =G01NHA01KF002+U012UBB01UC002-KF02 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | B10:YB11 | YB11B | 05 | =G01NHA01QZ004-QB01&EFS.003 |  |  |  | U012UBB01UC002
=G01NHA01QZ004 | G01NHA01QZ004-QB01 | =G01NHA01QZ004-QB01;YB12 | ELY1 RECT1 DC SWG4 DISC DC+ CMD OFF/CL | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 4 DISCONNECTOR - DC+ MANUAL COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 004 | DC-Switchgear 4 | -QB01 | Disconnector - DC+ | YB12 | Manual command OFF/CLOSE | Ely1 | Rect1 | DC Swg4 | Disc DC+ | CMD OFF/CL | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | NS | [13 empty] | Yes |  | =G01NHA01KF002+U012UBB01UC002-KF02 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | B10:YB12 | YB12 | 06 | =G01NHA01QZ004-QB01&EFS.003 |  |  |  | U012UBB01UC002
=G01NHA01QZ004 | G01NHA01QZ004-QB02 | =G01NHA01QZ004-QB02;YB11 | ELY1 RECT1 DC SWG4 DISC DC- CMD ON/OP | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 4 DISCONNECTOR - DC- MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 004 | DC-Switchgear 4 | -QB02 | Disconnector - DC- | YB11 | Manual command ON/OPEN | Ely1 | Rect1 | DC Swg4 | Disc DC- | CMD ON/OP | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | NS | [13 empty] | Yes |  | =G01NHA01KF002+U012UBB01UC002-KF02 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | B10:YB11 | YB11 | 07 | =G01NHA01QZ004-QB02&EFS.004 |  |  |  | U012UBB01UC002
=G01NHA01QZ004 | G01NHA01QZ004-QB02 | =G01NHA01QZ004-QB02;YB12 | ELY1 RECT1 DC SWG4 DISC DC- CMD OFF/CL | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 DC-SWITCHGEAR DC-SWITCHGEAR 4 DISCONNECTOR - DC- MANUAL COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | QZ | DC-Switchgear | 004 | DC-Switchgear 4 | -QB02 | Disconnector - DC- | YB12 | Manual command OFF/CLOSE | Ely1 | Rect1 | DC Swg4 | Disc DC- | CMD OFF/CL | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | NS | [13 empty] | Yes |  | =G01NHA01KF002+U012UBB01UC002-KF02 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | B10:YB12 | YB12 | 08 | =G01NHA01QZ004-QB02&EFS.004 |  |  |  | U012UBB01UC002
=G01NHA01RA001 | G01NHA01RA001-KF01 | =G01NHA01RA001-KF01;YB11 | ELY1 RECT1 DISCH RES1 OUTP MOD CMD ON/OP | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RESISTORS DISCHARGE-RESISTOR 1 OUTPUT COUPLER RELAY COUPLER, 1 CHANGE-OVER CONTACT MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | RA | Resistors | 001 | Discharge-Resistor 1 | -KF01 | Output coupler Relay coupler, 1 change-over contact | YB11 | Manual command ON/OPEN | Ely1 | Rect1 | Disch Res1 | Outp Mod | CMD ON/OP | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 0 | NS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF06 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 07 | =G01NHA01RA001-KF01&EFS.003 |  |  |  | U012UBB01UC001
=G01NHA01RA002 | G01NHA01RA002-KF01 | =G01NHA01RA002-KF01;YB11 | ELY1 RECT1 DISCH RES2 OUTP MOD CMD ON/OP | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RESISTORS DISCHARGE-RESISTOR 2 OUTPUT COUPLER RELAY COUPLER, 1 CHANGE-OVER CONTACT MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | RA | Resistors | 002 | Discharge-Resistor 2 | -KF01 | Output coupler Relay coupler, 1 change-over contact | YB11 | Manual command ON/OPEN | Ely1 | Rect1 | Disch Res2 | Outp Mod | CMD ON/OP | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 0 | NS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF06 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 08 | =G01NHA01RA002-KF01&EFS.003 |  |  |  | U012UBB01UC001
=G01NHA01RA003 | G01NHA01RA003-KF01 | =G01NHA01RA003-KF01;YB11 | ELY1 RECT1 DISCH RES3 OUTP MOD CMD ON/OP | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RESISTORS DISCHARGE-RESISTOR 3 OUTPUT COUPLER RELAY COUPLER, 1 CHANGE-OVER CONTACT MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | RA | Resistors | 003 | Discharge-Resistor 3 | -KF01 | Output coupler Relay coupler, 1 change-over contact | YB11 | Manual command ON/OPEN | Ely1 | Rect1 | Disch Res3 | Outp Mod | CMD ON/OP | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 0 | NS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF05 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 01 | =G01NHA01RA003-KF01&EFS.003 |  |  |  | U012UBB01UC002
=G01NHA01RA004 | G01NHA01RA004-KF01 | =G01NHA01RA004-KF01;YB11 | ELY1 RECT1 DISCH RES4 OUTP MOD CMD ON/OP | 40 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RESISTORS DISCHARGE-RESISTOR 4 OUTPUT COUPLER RELAY COUPLER, 1 CHANGE-OVER CONTACT MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | RA | Resistors | 004 | Discharge-Resistor 4 | -KF01 | Output coupler Relay coupler, 1 change-over contact | YB11 | Manual command ON/OPEN | Ely1 | Rect1 | Disch Res4 | Outp Mod | CMD ON/OP | -XG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 0 | NS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF05 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 02 | =G01NHA01RA004-KF01&EFS.003 |  |  |  | U012UBB01UC002
=G01NHA01TA001 | G01NHA01TA001-GP01 | =G01NHA01TA001-GP01;YB11 | ELY1 RECT1 TRAFO1 PMP1 CMD ON/OP | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER OIL PUMP - TRANSFORMER MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -GP01 | Oil Pump - Transformer | YB11 | Manual command ON/OPEN | Ely1 | Rect1 | Trafo1 | PMP1 | CMD ON/OP | -QA01 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 0 | YS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF06 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 04 | =G01NHA01TA001-GP01&EFS.008 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-QA01 | =G01NHA01TA001-QA01;YB11 | ELY1 RECT1 TRAFO1 SW1 CMD ON/OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER TAP CHANGER MANUEL COMMAND LOWER | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -QA01 | Tap Changer | YB11 | Manuel command LOWER | Ely1 | Rect1 | Trafo1 | Sw1 | CMD ON/OP | -KF01 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 0 | YS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF06 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 05 | =G01NHA01TA001-QA01&EFS.002 |  |  |  | U012UBB01UC001
=G01NHA01TA001 | G01NHA01TA001-QA01 | =G01NHA01TA001-QA01;YB12 | ELY1 RECT1 TRAFO1 SW1 CMD OFF/CL | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 TRANSFORMERS RECTIFIER TRANSFORMER TAP CHANGER MANUEL COMMAND HIGHER | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TA | Transformers | 001 | Rectifier Transformer | -QA01 | Tap Changer | YB12 | Manuel command HIGHER | Ely1 | Rect1 | Trafo1 | Sw1 | CMD OFF/CL | -KF02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 0 | YS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF06 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB12 | EA01 | 06 | =G01NHA01TA001-QA01&EFS.002 |  |  |  | U012UBB01UC001
=G01NHA01TB001 | G01NHA01TB001-GQ01 | =G01NHA01TB001-GQ01;YB11 | ELY1 RECT1 RECT1 RAD BLOW CMD ON/OP | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 1 RADIAL BLOWER MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 001 | Rectifier 1 | -GQ01 | Radial blower | YB11 | Manual command ON/OPEN | Ely1 | Rect1 | Rect1 | Rad Blow | CMD ON/OP |  | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 0 | NS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF06 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 09 |  |  |  |  | U012UBB01UC001
=G01NHA01TB001 | G01NHA01TB001-KF01 | =G01NHA01TB001-KF01;YW01 | ELY1 RECT1 RECT1 OUTP MOD AL/PROT1 | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 1 SINAMICS DCM CONTROL MODULE WITHOUT POWER SECTION COMPONENT PROTECTION | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 001 | Rectifier 1 | -KF01 | SINAMICS DCM CONTROL MODULE WITHOUT POWER SECTION | YW01 | Component protection | Ely1 | Rect1 | Rect1 | Outp Mod | AL/PROT1 | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | YZ | [13 empty] | Yes | SIL 2 | =G01NHA01KF001+U012UBB01UC001-KF02 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | B10:YW01 | YW01 | 09 | =G01NHA01TB001-KF01&EFS.001 | =G01NHA01&MFB.001 |  |  | U012UBB01UC001
=G01NHA01TB002 | G01NHA01TB002-GQ01 | =G01NHA01TB002-GQ01;YB11 | ELY1 RECT1 RECT2 RAD BLOW CMD ON/OP | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 2 RADIAL BLOWER MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 002 | Rectifier 2 | -GQ01 | Radial blower | YB11 | Manual command ON/OPEN | Ely1 | Rect1 | Rect2 | Rad Blow | CMD ON/OP |  | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 0 | NS | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF06 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 10 |  |  |  |  | U012UBB01UC001
=G01NHA01TB002 | G01NHA01TB002-KF01 | =G01NHA01TB002-KF01;YW01 | ELY1 RECT1 RECT2 OUTP MOD AL/PROT1 | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 2 SINAMICS DCM CONTROL MODULE WITHOUT POWER SECTION COMPONENT PROTECTION | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 002 | Rectifier 2 | -KF01 | SINAMICS DCM CONTROL MODULE WITHOUT POWER SECTION | YW01 | Component protection | Ely1 | Rect1 | Rect2 | Outp Mod | AL/PROT1 | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | YZ | [13 empty] | Yes | SIL 2 | =G01NHA01KF001+U012UBB01UC001-KF02 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | B10:YW01 | YW01 | 10 | =G01NHA01TB002-KF01&EFS.001 | =G01NHA01&MFB.001 |  |  | U012UBB01UC001
=G01NHA01TB003 | G01NHA01TB003-GQ01 | =G01NHA01TB003-GQ01;YB11 | ELY1 RECT1 RECT3 RAD BLOW CMD ON/OP | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 3 RADIAL BLOWER MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 003 | Rectifier 3 | -GQ01 | Radial blower | YB11 | Manual command ON/OPEN | Ely1 | Rect1 | Rect3 | Rad Blow | CMD ON/OP |  | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 0 | NS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF05 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 03 |  |  |  |  | U012UBB01UC002
=G01NHA01TB003 | G01NHA01TB003-KF01 | =G01NHA01TB003-KF01;YW01 | ELY1 RECT1 RECT3 OUTP MOD AL/PROT1 | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 3 SINAMICS DCM CONTROL MODULE WITHOUT POWER SECTION COMPONENT PROTECTION | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 003 | Rectifier 3 | -KF01 | SINAMICS DCM CONTROL MODULE WITHOUT POWER SECTION | YW01 | Component protection | Ely1 | Rect1 | Rect3 | Outp Mod | AL/PROT1 | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | YZ | [13 empty] | Yes | SIL 2 | =G01NHA01KF002+U012UBB01UC002-KF02 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | B10:YW01 | YW01 | 09 | =G01NHA01TB003-KF01&EFS.001 | =G01NHA01&MFB.001 |  |  | U012UBB01UC002
=G01NHA01TB004 | G01NHA01TB004-GQ01 | =G01NHA01TB004-GQ01;YB11 | ELY1 RECT1 RECT4 RAD BLOW CMD ON/OP | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 4 RADIAL BLOWER MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 004 | Rectifier 4 | -GQ01 | Radial blower | YB11 | Manual command ON/OPEN | Ely1 | Rect1 | Rect4 | Rad Blow | CMD ON/OP |  | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 0 | NS | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF05 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 04 |  |  |  |  | U012UBB01UC002
=G01NHA01TB004 | G01NHA01TB004-KF01 | =G01NHA01TB004-KF01;YW01 | ELY1 RECT1 RECT4 OUTP MOD AL/PROT1 | 34 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 4 SINAMICS DCM CONTROL MODULE WITHOUT POWER SECTION COMPONENT PROTECTION | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 004 | Rectifier 4 | -KF01 | SINAMICS DCM CONTROL MODULE WITHOUT POWER SECTION | YW01 | Component protection | Ely1 | Rect1 | Rect4 | Outp Mod | AL/PROT1 | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | YZ | [13 empty] | Yes | SIL 2 | =G01NHA01KF002+U012UBB01UC002-KF02 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | B10:YW01 | YW01 | 10 | =G01NHA01TB004-KF01&EFS.001 | =G01NHA01&MFB.001 |  |  | U012UBB01UC002
=G01NHA01TB011 | G01NHA01TB011-KF11 | =G01NHA01TB011-KF11;YB32 | ELY1 RECT1 POLR1 DCM1 PROT CMD OFF/CLD | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 1&2 SINAMICS DCM - STO PROTECTION COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 011 | Polarisation Rectifier System 1&2 | -KF11 | SINAMICS DCM - STO | YB32 | Protection Command OFF/CLOSE | Ely1 | Rect1 | Polr1 | DCM1 | PROT CMD OFF/CLD | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | YSC | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | XG03:1 | 1B | 04 | =G01NHA01TB011-KF11&EFS.001 | =G01NHA01&MFB.001 |  |  | U012UBB01UC001
=G01NHA01TB011 | G01NHA01TB011-KF12 | =G01NHA01TB011-KF12;YB32 | ELY1 RECT1 POLR1 DCM2 PROT CMD OFF/CLD | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 1&2 SINAMICS DCM - STO PROTECTION COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 011 | Polarisation Rectifier System 1&2 | -KF12 | SINAMICS DCM - STO | YB32 | Protection Command OFF/CLOSE | Ely1 | Rect1 | Polr1 | DCM2 | PROT CMD OFF/CLD | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | YSC | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | XG03:9 | 9B | 05 | =G01NHA01TB011-KF12&EFS.001 | =G01NHA01&MFB.001 |  |  | U012UBB01UC001
=G01NHA01TB011 | G01NHA01TB011-QA03 | =G01NHA01TB011-QA03;YB32 | ELY1 RECT1 POLR1 SW3 PROT CMD OFF/CLD | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 1&2 MAINSWITCH - OFF PROTECTION COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 011 | Polarisation Rectifier System 1&2 | -QA03 | Mainswitch - OFF | YB32 | Protection Command OFF/CLOSE | Ely1 | Rect1 | Polr1 | Sw3 | PROT CMD OFF/CLD | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | YSC | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | XG03:5 | 5B | 06 | =G01NHA01TB011-QA03&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01TB011 | G01NHA01TB011-QA04 | =G01NHA01TB011-QA04;YB32 | ELY1 RECT1 POLR1 SW4 PROT CMD OFF/CLD | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 1&2 MAINSWITCH - OFF PROTECTION COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 011 | Polarisation Rectifier System 1&2 | -QA04 | Mainswitch - OFF | YB32 | Protection Command OFF/CLOSE | Ely1 | Rect1 | Polr1 | Sw4 | PROT CMD OFF/CLD | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | YSC | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | XG03:13 | 13B | 07 | =G01NHA01TB011-QA04&EFS.001 |  |  |  | U012UBB01UC001
=G01NHA01TB012 | G01NHA01TB012-KF11 | =G01NHA01TB012-KF11;YB32 | ELY1 RECT1 POLR2 DCM1 PROT CMD OFF/CLD | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 3&4 SINAMICS DCM - STO PROTECTION COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 012 | Polarisation Rectifier System 3&4 | -KF11 | SINAMICS DCM - STO | YB32 | Protection Command OFF/CLOSE | Ely1 | Rect1 | Polr2 | DCM1 | PROT CMD OFF/CLD | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | YSC | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF03 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | XG03:1 | 1B | 01 | =G01NHA01TB012-KF11&EFS.001 | =G01NHA01&MFB.001 |  |  | U012UBB01UC002
=G01NHA01TB012 | G01NHA01TB012-KF12 | =G01NHA01TB012-KF12;YB32 | ELY1 RECT1 POLR2 DCM2 PROT CMD OFF/CLD | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 3&4 SINAMICS DCM - STO PROTECTION COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 012 | Polarisation Rectifier System 3&4 | -KF12 | SINAMICS DCM - STO | YB32 | Protection Command OFF/CLOSE | Ely1 | Rect1 | Polr2 | DCM2 | PROT CMD OFF/CLD | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | YSC | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF03 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | XG03:9 | 9B | 02 | =G01NHA01TB012-KF12&EFS.001 | =G01NHA01&MFB.001 |  |  | U012UBB01UC002
=G01NHA01TB012 | G01NHA01TB012-QA03 | =G01NHA01TB012-QA03;YB32 | ELY1 RECT1 POLR2 SW3 PROT CMD OFF/CLD | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 3&4 MAINSWITCH - OFF PROTECTION COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 012 | Polarisation Rectifier System 3&4 | -QA03 | Mainswitch - OFF | YB32 | Protection Command OFF/CLOSE | Ely1 | Rect1 | Polr2 | Sw3 | PROT CMD OFF/CLD | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | YSC | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF03 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | XG03:5 | 5B | 03 | =G01NHA01TB012-QA03&EFS.001 |  |  |  | U012UBB01UC002
=G01NHA01TB012 | G01NHA01TB012-QA04 | =G01NHA01TB012-QA04;YB32 | ELY1 RECT1 POLR2 SW4 PROT CMD OFF/CLD | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS POLARISATION RECTIFIER SYSTEM 3&4 MAINSWITCH - OFF PROTECTION COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 012 | Polarisation Rectifier System 3&4 | -QA04 | Mainswitch - OFF | YB32 | Protection Command OFF/CLOSE | Ely1 | Rect1 | Polr2 | Sw4 | PROT CMD OFF/CLD | -XG03 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 1 | YSC | [15 empty] | =G01NHA01KF002+U012UBB01UC002-KF03 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | XG03:13 | 13B | 04 | =G01NHA01TB012-QA04&EFS.001 |  |  |  | U012UBB01UC002
=G01NHB01KF001 | G01NHB01KF001-BA01 | =G01NHB01KF001-BA01;YS10 | ELY1 GRP1 CTRL U1 CELL VOLT1 CHAN TRF | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS TRANSFER | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS10 | Command - Channel adress transfer | Ely1 | Grp1 | CTRL U1 | Cell Volt1 | CHAN TRF | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB01KF001+U012UNA01UH112-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 01 | =G01NHB01KF001&EFS.051 | =G01NHB01&MFB.001 |  |  | U012UNA01UH112
=G01NHB01KF001 | G01NHB01KF001-BA01 | =G01NHB01KF001-BA01;YS11 | ELY1 GRP1 CTRL U1 CELL VOLT1 CHAN ADR | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS ACTIVE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS11 | Command - Channel adress active | Ely1 | Grp1 | CTRL U1 | Cell Volt1 | CHAN ADR | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB01KF001+U012UNA01UH112-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 02 | =G01NHB01KF001&EFS.051 | =G01NHB01&MFB.001 |  |  | U012UNA01UH112
=G01NHB01KF001 | G01NHB01KF001-BA01 | =G01NHB01KF001-BA01;YS01 | ELY1 GRP1 CTRL U1 CELL VOLT1 CHAN BIT1 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS01 | Command - Channel adress Bit 1 | Ely1 | Grp1 | CTRL U1 | Cell Volt1 | CHAN BIT1 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB01KF001+U012UNA01UH112-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 03 | =G01NHB01KF001&EFS.051 | =G01NHB01&MFB.001 |  |  | U012UNA01UH112
=G01NHB01KF001 | G01NHB01KF001-BA01 | =G01NHB01KF001-BA01;YS02 | ELY1 GRP1 CTRL U1 CELL VOLT1 CHAN BIT2 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 2 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS02 | Command - Channel adress Bit 2 | Ely1 | Grp1 | CTRL U1 | Cell Volt1 | CHAN BIT2 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB01KF001+U012UNA01UH112-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 04 | =G01NHB01KF001&EFS.051 | =G01NHB01&MFB.001 |  |  | U012UNA01UH112
=G01NHB01KF001 | G01NHB01KF001-BA01 | =G01NHB01KF001-BA01;YS03 | ELY1 GRP1 CTRL U1 CELL VOLT1 CHAN BIT3 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 3 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS03 | Command - Channel adress Bit 3 | Ely1 | Grp1 | CTRL U1 | Cell Volt1 | CHAN BIT3 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB01KF001+U012UNA01UH112-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 05 | =G01NHB01KF001&EFS.052 | =G01NHB01&MFB.001 |  |  | U012UNA01UH112
=G01NHB01KF001 | G01NHB01KF001-BA01 | =G01NHB01KF001-BA01;YS04 | ELY1 GRP1 CTRL U1 CELL VOLT1 CHAN BIT4 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 4 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS04 | Command - Channel adress Bit 4 | Ely1 | Grp1 | CTRL U1 | Cell Volt1 | CHAN BIT4 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB01KF001+U012UNA01UH112-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 06 | =G01NHB01KF001&EFS.052 | =G01NHB01&MFB.001 |  |  | U012UNA01UH112
=G01NHB01KF001 | G01NHB01KF001-BA01 | =G01NHB01KF001-BA01;YS05 | ELY1 GRP1 CTRL U1 CELL VOLT1 CHAN BIT5 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 5 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS05 | Command - Channel adress Bit 5 | Ely1 | Grp1 | CTRL U1 | Cell Volt1 | CHAN BIT5 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB01KF001+U012UNA01UH112-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 07 | =G01NHB01KF001&EFS.052 | =G01NHB01&MFB.001 |  |  | U012UNA01UH112
=G01NHB01KF001 | G01NHB01KF001-BA01 | =G01NHB01KF001-BA01;YS06 | ELY1 GRP1 CTRL U1 CELL VOLT1 CHAN BIT6 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 1 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 6 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 01 | Module Group 1 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS06 | Command - Channel adress Bit 6 | Ely1 | Grp1 | CTRL U1 | Cell Volt1 | CHAN BIT6 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB01KF001+U012UNA01UH112-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 08 | =G01NHB01KF001&EFS.052 | =G01NHB01&MFB.001 |  |  | U012UNA01UH112
=G01NHB02KF001 | G01NHB02KF001-BA01 | =G01NHB02KF001-BA01;YS10 | ELY1 GRP2 CTRL U1 CELL VOLT1 CHAN TRF | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS TRANSFER | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS10 | Command - Channel adress transfer | Ely1 | Grp2 | CTRL U1 | Cell Volt1 | CHAN TRF | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB02KF001+U012UNA01UH122-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 07 | =G01NHB02KF001&EFS.052 | =G01NHB02&MFB.001 |  |  | U012UNA01UH122
=G01NHB02KF001 | G01NHB02KF001-BA01 | =G01NHB02KF001-BA01;YS11 | ELY1 GRP2 CTRL U1 CELL VOLT1 CHAN ADR | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS ACTIVE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS11 | Command - Channel adress active | Ely1 | Grp2 | CTRL U1 | Cell Volt1 | CHAN ADR | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB02KF001+U012UNA01UH122-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 08 | =G01NHB02KF001&EFS.052 | =G01NHB02&MFB.001 |  |  | U012UNA01UH122
=G01NHB02KF001 | G01NHB02KF001-BA01 | =G01NHB02KF001-BA01;YS01 | ELY1 GRP2 CTRL U1 CELL VOLT1 CHAN BIT1 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS01 | Command - Channel adress Bit 1 | Ely1 | Grp2 | CTRL U1 | Cell Volt1 | CHAN BIT1 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB02KF001+U012UNA01UH122-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 01 | =G01NHB02KF001&EFS.051 | =G01NHB02&MFB.001 |  |  | U012UNA01UH122
=G01NHB02KF001 | G01NHB02KF001-BA01 | =G01NHB02KF001-BA01;YS02 | ELY1 GRP2 CTRL U1 CELL VOLT1 CHAN BIT2 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 2 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS02 | Command - Channel adress Bit 2 | Ely1 | Grp2 | CTRL U1 | Cell Volt1 | CHAN BIT2 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB02KF001+U012UNA01UH122-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 02 | =G01NHB02KF001&EFS.051 | =G01NHB02&MFB.001 |  |  | U012UNA01UH122
=G01NHB02KF001 | G01NHB02KF001-BA01 | =G01NHB02KF001-BA01;YS03 | ELY1 GRP2 CTRL U1 CELL VOLT1 CHAN BIT3 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 3 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS03 | Command - Channel adress Bit 3 | Ely1 | Grp2 | CTRL U1 | Cell Volt1 | CHAN BIT3 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB02KF001+U012UNA01UH122-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 03 | =G01NHB02KF001&EFS.051 | =G01NHB02&MFB.001 |  |  | U012UNA01UH122
=G01NHB02KF001 | G01NHB02KF001-BA01 | =G01NHB02KF001-BA01;YS04 | ELY1 GRP2 CTRL U1 CELL VOLT1 CHAN BIT4 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 4 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS04 | Command - Channel adress Bit 4 | Ely1 | Grp2 | CTRL U1 | Cell Volt1 | CHAN BIT4 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB02KF001+U012UNA01UH122-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 04 | =G01NHB02KF001&EFS.051 | =G01NHB02&MFB.001 |  |  | U012UNA01UH122
=G01NHB02KF001 | G01NHB02KF001-BA01 | =G01NHB02KF001-BA01;YS05 | ELY1 GRP2 CTRL U1 CELL VOLT1 CHAN BIT5 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 5 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS05 | Command - Channel adress Bit 5 | Ely1 | Grp2 | CTRL U1 | Cell Volt1 | CHAN BIT5 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB02KF001+U012UNA01UH122-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 05 | =G01NHB02KF001&EFS.052 | =G01NHB02&MFB.001 |  |  | U012UNA01UH122
=G01NHB02KF001 | G01NHB02KF001-BA01 | =G01NHB02KF001-BA01;YS06 | ELY1 GRP2 CTRL U1 CELL VOLT1 CHAN BIT6 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 2 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 6 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 02 | Module Group 2 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS06 | Command - Channel adress Bit 6 | Ely1 | Grp2 | CTRL U1 | Cell Volt1 | CHAN BIT6 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB02KF001+U012UNA01UH122-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 06 | =G01NHB02KF001&EFS.052 | =G01NHB02&MFB.001 |  |  | U012UNA01UH122
=G01NHB03KF001 | G01NHB03KF001-BA01 | =G01NHB03KF001-BA01;YS10 | ELY1 GRP3 CTRL U1 CELL VOLT1 CHAN TRF | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS TRANSFER | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS10 | Command - Channel adress transfer | Ely1 | Grp3 | CTRL U1 | Cell Volt1 | CHAN TRF | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB03KF001+U012UNA01UH132-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 07 | =G01NHB03KF001&EFS.052 | =G01NHB03&MFB.001 |  |  | U012UNA01UH132
=G01NHB03KF001 | G01NHB03KF001-BA01 | =G01NHB03KF001-BA01;YS11 | ELY1 GRP3 CTRL U1 CELL VOLT1 CHAN ADR | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS ACTIVE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS11 | Command - Channel adress active | Ely1 | Grp3 | CTRL U1 | Cell Volt1 | CHAN ADR | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB03KF001+U012UNA01UH132-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 08 | =G01NHB03KF001&EFS.052 | =G01NHB03&MFB.001 |  |  | U012UNA01UH132
=G01NHB03KF001 | G01NHB03KF001-BA01 | =G01NHB03KF001-BA01;YS01 | ELY1 GRP3 CTRL U1 CELL VOLT1 CHAN BIT1 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS01 | Command - Channel adress Bit 1 | Ely1 | Grp3 | CTRL U1 | Cell Volt1 | CHAN BIT1 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB03KF001+U012UNA01UH132-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 01 | =G01NHB03KF001&EFS.051 | =G01NHB03&MFB.001 |  |  | U012UNA01UH132
=G01NHB03KF001 | G01NHB03KF001-BA01 | =G01NHB03KF001-BA01;YS02 | ELY1 GRP3 CTRL U1 CELL VOLT1 CHAN BIT2 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 2 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS02 | Command - Channel adress Bit 2 | Ely1 | Grp3 | CTRL U1 | Cell Volt1 | CHAN BIT2 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB03KF001+U012UNA01UH132-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 02 | =G01NHB03KF001&EFS.051 | =G01NHB03&MFB.001 |  |  | U012UNA01UH132
=G01NHB03KF001 | G01NHB03KF001-BA01 | =G01NHB03KF001-BA01;YS03 | ELY1 GRP3 CTRL U1 CELL VOLT1 CHAN BIT3 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 3 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS03 | Command - Channel adress Bit 3 | Ely1 | Grp3 | CTRL U1 | Cell Volt1 | CHAN BIT3 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB03KF001+U012UNA01UH132-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 03 | =G01NHB03KF001&EFS.051 | =G01NHB03&MFB.001 |  |  | U012UNA01UH132
=G01NHB03KF001 | G01NHB03KF001-BA01 | =G01NHB03KF001-BA01;YS04 | ELY1 GRP3 CTRL U1 CELL VOLT1 CHAN BIT4 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 4 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS04 | Command - Channel adress Bit 4 | Ely1 | Grp3 | CTRL U1 | Cell Volt1 | CHAN BIT4 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB03KF001+U012UNA01UH132-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 04 | =G01NHB03KF001&EFS.051 | =G01NHB03&MFB.001 |  |  | U012UNA01UH132
=G01NHB03KF001 | G01NHB03KF001-BA01 | =G01NHB03KF001-BA01;YS05 | ELY1 GRP3 CTRL U1 CELL VOLT1 CHAN BIT5 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 5 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS05 | Command - Channel adress Bit 5 | Ely1 | Grp3 | CTRL U1 | Cell Volt1 | CHAN BIT5 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB03KF001+U012UNA01UH132-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 05 | =G01NHB03KF001&EFS.052 | =G01NHB03&MFB.001 |  |  | U012UNA01UH132
=G01NHB03KF001 | G01NHB03KF001-BA01 | =G01NHB03KF001-BA01;YS06 | ELY1 GRP3 CTRL U1 CELL VOLT1 CHAN BIT6 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 3 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 6 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 03 | Module Group 3 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS06 | Command - Channel adress Bit 6 | Ely1 | Grp3 | CTRL U1 | Cell Volt1 | CHAN BIT6 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB03KF001+U012UNA01UH132-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 06 | =G01NHB03KF001&EFS.052 | =G01NHB03&MFB.001 |  |  | U012UNA01UH132
=G01NHB04KF001 | G01NHB04KF001-BA01 | =G01NHB04KF001-BA01;YS10 | ELY1 GRP4 CTRL U1 CELL VOLT1 CHAN TRF | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS TRANSFER | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS10 | Command - Channel adress transfer | Ely1 | Grp4 | CTRL U1 | Cell Volt1 | CHAN TRF | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB04KF001+U012UNA01UH142-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 07 | =G01NHB04KF001&EFS.052 | =G01NHB04&MFB.001 |  |  | U012UNA01UH142
=G01NHB04KF001 | G01NHB04KF001-BA01 | =G01NHB04KF001-BA01;YS11 | ELY1 GRP4 CTRL U1 CELL VOLT1 CHAN ADR | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS ACTIVE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS11 | Command - Channel adress active | Ely1 | Grp4 | CTRL U1 | Cell Volt1 | CHAN ADR | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB04KF001+U012UNA01UH142-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 08 | =G01NHB04KF001&EFS.052 | =G01NHB04&MFB.001 |  |  | U012UNA01UH142
=G01NHB04KF001 | G01NHB04KF001-BA01 | =G01NHB04KF001-BA01;YS01 | ELY1 GRP4 CTRL U1 CELL VOLT1 CHAN BIT1 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS01 | Command - Channel adress Bit 1 | Ely1 | Grp4 | CTRL U1 | Cell Volt1 | CHAN BIT1 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB04KF001+U012UNA01UH142-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 01 | =G01NHB04KF001&EFS.051 | =G01NHB04&MFB.001 |  |  | U012UNA01UH142
=G01NHB04KF001 | G01NHB04KF001-BA01 | =G01NHB04KF001-BA01;YS02 | ELY1 GRP4 CTRL U1 CELL VOLT1 CHAN BIT2 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 2 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS02 | Command - Channel adress Bit 2 | Ely1 | Grp4 | CTRL U1 | Cell Volt1 | CHAN BIT2 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB04KF001+U012UNA01UH142-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 02 | =G01NHB04KF001&EFS.051 | =G01NHB04&MFB.001 |  |  | U012UNA01UH142
=G01NHB04KF001 | G01NHB04KF001-BA01 | =G01NHB04KF001-BA01;YS03 | ELY1 GRP4 CTRL U1 CELL VOLT1 CHAN BIT3 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 3 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS03 | Command - Channel adress Bit 3 | Ely1 | Grp4 | CTRL U1 | Cell Volt1 | CHAN BIT3 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB04KF001+U012UNA01UH142-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 03 | =G01NHB04KF001&EFS.051 | =G01NHB04&MFB.001 |  |  | U012UNA01UH142
=G01NHB04KF001 | G01NHB04KF001-BA01 | =G01NHB04KF001-BA01;YS04 | ELY1 GRP4 CTRL U1 CELL VOLT1 CHAN BIT4 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 4 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS04 | Command - Channel adress Bit 4 | Ely1 | Grp4 | CTRL U1 | Cell Volt1 | CHAN BIT4 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB04KF001+U012UNA01UH142-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 04 | =G01NHB04KF001&EFS.051 | =G01NHB04&MFB.001 |  |  | U012UNA01UH142
=G01NHB04KF001 | G01NHB04KF001-BA01 | =G01NHB04KF001-BA01;YS05 | ELY1 GRP4 CTRL U1 CELL VOLT1 CHAN BIT5 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 5 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS05 | Command - Channel adress Bit 5 | Ely1 | Grp4 | CTRL U1 | Cell Volt1 | CHAN BIT5 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB04KF001+U012UNA01UH142-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 05 | =G01NHB04KF001&EFS.052 | =G01NHB04&MFB.001 |  |  | U012UNA01UH142
=G01NHB04KF001 | G01NHB04KF001-BA01 | =G01NHB04KF001-BA01;YS06 | ELY1 GRP4 CTRL U1 CELL VOLT1 CHAN BIT6 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 4 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 6 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 04 | Module Group 4 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS06 | Command - Channel adress Bit 6 | Ely1 | Grp4 | CTRL U1 | Cell Volt1 | CHAN BIT6 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB04KF001+U012UNA01UH142-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 06 | =G01NHB04KF001&EFS.052 | =G01NHB04&MFB.001 |  |  | U012UNA01UH142
=G01NHB05KF001 | G01NHB05KF001-BA01 | =G01NHB05KF001-BA01;YS10 | ELY1 GRP5 CTRL U1 CELL VOLT1 CHAN TRF | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS TRANSFER | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS10 | Command - Channel adress transfer | Ely1 | Grp5 | CTRL U1 | Cell Volt1 | CHAN TRF | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB05KF001+U012UNA01UH152-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 07 | =G01NHB05KF001&EFS.052 | =G01NHB05&MFB.001 |  |  | U012UNA01UH152
=G01NHB05KF001 | G01NHB05KF001-BA01 | =G01NHB05KF001-BA01;YS11 | ELY1 GRP5 CTRL U1 CELL VOLT1 CHAN ADR | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS ACTIVE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS11 | Command - Channel adress active | Ely1 | Grp5 | CTRL U1 | Cell Volt1 | CHAN ADR | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB05KF001+U012UNA01UH152-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 08 | =G01NHB05KF001&EFS.052 | =G01NHB05&MFB.001 |  |  | U012UNA01UH152
=G01NHB05KF001 | G01NHB05KF001-BA01 | =G01NHB05KF001-BA01;YS01 | ELY1 GRP5 CTRL U1 CELL VOLT1 CHAN BIT1 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS01 | Command - Channel adress Bit 1 | Ely1 | Grp5 | CTRL U1 | Cell Volt1 | CHAN BIT1 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB05KF001+U012UNA01UH152-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 01 | =G01NHB05KF001&EFS.051 | =G01NHB05&MFB.001 |  |  | U012UNA01UH152
=G01NHB05KF001 | G01NHB05KF001-BA01 | =G01NHB05KF001-BA01;YS02 | ELY1 GRP5 CTRL U1 CELL VOLT1 CHAN BIT2 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 2 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS02 | Command - Channel adress Bit 2 | Ely1 | Grp5 | CTRL U1 | Cell Volt1 | CHAN BIT2 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB05KF001+U012UNA01UH152-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 02 | =G01NHB05KF001&EFS.051 | =G01NHB05&MFB.001 |  |  | U012UNA01UH152
=G01NHB05KF001 | G01NHB05KF001-BA01 | =G01NHB05KF001-BA01;YS03 | ELY1 GRP5 CTRL U1 CELL VOLT1 CHAN BIT3 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 3 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS03 | Command - Channel adress Bit 3 | Ely1 | Grp5 | CTRL U1 | Cell Volt1 | CHAN BIT3 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB05KF001+U012UNA01UH152-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 03 | =G01NHB05KF001&EFS.051 | =G01NHB05&MFB.001 |  |  | U012UNA01UH152
=G01NHB05KF001 | G01NHB05KF001-BA01 | =G01NHB05KF001-BA01;YS04 | ELY1 GRP5 CTRL U1 CELL VOLT1 CHAN BIT4 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 4 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS04 | Command - Channel adress Bit 4 | Ely1 | Grp5 | CTRL U1 | Cell Volt1 | CHAN BIT4 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB05KF001+U012UNA01UH152-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 04 | =G01NHB05KF001&EFS.051 | =G01NHB05&MFB.001 |  |  | U012UNA01UH152
=G01NHB05KF001 | G01NHB05KF001-BA01 | =G01NHB05KF001-BA01;YS05 | ELY1 GRP5 CTRL U1 CELL VOLT1 CHAN BIT5 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 5 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS05 | Command - Channel adress Bit 5 | Ely1 | Grp5 | CTRL U1 | Cell Volt1 | CHAN BIT5 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB05KF001+U012UNA01UH152-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 05 | =G01NHB05KF001&EFS.052 | =G01NHB05&MFB.001 |  |  | U012UNA01UH152
=G01NHB05KF001 | G01NHB05KF001-BA01 | =G01NHB05KF001-BA01;YS06 | ELY1 GRP5 CTRL U1 CELL VOLT1 CHAN BIT6 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 5 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 6 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 05 | Module Group 5 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS06 | Command - Channel adress Bit 6 | Ely1 | Grp5 | CTRL U1 | Cell Volt1 | CHAN BIT6 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB05KF001+U012UNA01UH152-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 06 | =G01NHB05KF001&EFS.052 | =G01NHB05&MFB.001 |  |  | U012UNA01UH152
=G01NHB06KF001 | G01NHB06KF001-BA01 | =G01NHB06KF001-BA01;YS10 | ELY1 GRP6 CTRL U1 CELL VOLT1 CHAN TRF | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS TRANSFER | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS10 | Command - Channel adress transfer | Ely1 | Grp6 | CTRL U1 | Cell Volt1 | CHAN TRF | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB06KF001+U012UNA01UH162-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 07 | =G01NHB06KF001&EFS.052 | =G01NHB06&MFB.001 |  |  | U012UNA01UH162
=G01NHB06KF001 | G01NHB06KF001-BA01 | =G01NHB06KF001-BA01;YS11 | ELY1 GRP6 CTRL U1 CELL VOLT1 CHAN ADR | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS ACTIVE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS11 | Command - Channel adress active | Ely1 | Grp6 | CTRL U1 | Cell Volt1 | CHAN ADR | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB06KF001+U012UNA01UH162-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 08 | =G01NHB06KF001&EFS.052 | =G01NHB06&MFB.001 |  |  | U012UNA01UH162
=G01NHB06KF001 | G01NHB06KF001-BA01 | =G01NHB06KF001-BA01;YS01 | ELY1 GRP6 CTRL U1 CELL VOLT1 CHAN BIT1 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS01 | Command - Channel adress Bit 1 | Ely1 | Grp6 | CTRL U1 | Cell Volt1 | CHAN BIT1 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB06KF001+U012UNA01UH162-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 01 | =G01NHB06KF001&EFS.051 | =G01NHB06&MFB.001 |  |  | U012UNA01UH162
=G01NHB06KF001 | G01NHB06KF001-BA01 | =G01NHB06KF001-BA01;YS02 | ELY1 GRP6 CTRL U1 CELL VOLT1 CHAN BIT2 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 2 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS02 | Command - Channel adress Bit 2 | Ely1 | Grp6 | CTRL U1 | Cell Volt1 | CHAN BIT2 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB06KF001+U012UNA01UH162-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 02 | =G01NHB06KF001&EFS.051 | =G01NHB06&MFB.001 |  |  | U012UNA01UH162
=G01NHB06KF001 | G01NHB06KF001-BA01 | =G01NHB06KF001-BA01;YS03 | ELY1 GRP6 CTRL U1 CELL VOLT1 CHAN BIT3 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 3 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS03 | Command - Channel adress Bit 3 | Ely1 | Grp6 | CTRL U1 | Cell Volt1 | CHAN BIT3 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB06KF001+U012UNA01UH162-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 03 | =G01NHB06KF001&EFS.051 | =G01NHB06&MFB.001 |  |  | U012UNA01UH162
=G01NHB06KF001 | G01NHB06KF001-BA01 | =G01NHB06KF001-BA01;YS04 | ELY1 GRP6 CTRL U1 CELL VOLT1 CHAN BIT4 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 4 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS04 | Command - Channel adress Bit 4 | Ely1 | Grp6 | CTRL U1 | Cell Volt1 | CHAN BIT4 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB06KF001+U012UNA01UH162-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 04 | =G01NHB06KF001&EFS.051 | =G01NHB06&MFB.001 |  |  | U012UNA01UH162
=G01NHB06KF001 | G01NHB06KF001-BA01 | =G01NHB06KF001-BA01;YS05 | ELY1 GRP6 CTRL U1 CELL VOLT1 CHAN BIT5 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 5 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS05 | Command - Channel adress Bit 5 | Ely1 | Grp6 | CTRL U1 | Cell Volt1 | CHAN BIT5 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB06KF001+U012UNA01UH162-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 05 | =G01NHB06KF001&EFS.052 | =G01NHB06&MFB.001 |  |  | U012UNA01UH162
=G01NHB06KF001 | G01NHB06KF001-BA01 | =G01NHB06KF001-BA01;YS06 | ELY1 GRP6 CTRL U1 CELL VOLT1 CHAN BIT6 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 ELECTROLYZER SYSTEM MODULE GROUP 6 CONTROL UNITS CELL VOLTAGE MEASUREMENT CELL-VOLTAGE-MEASUREMENT - MODULE 1 COMMAND - CHANNEL ADRESS BIT 6 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHB | Electrolyzer System | 06 | Module Group 6 | KF | Control Units | 001 | Cell Voltage Measurement | -BA01 | Cell-Voltage-Measurement - Module 1 | YS06 | Command - Channel adress Bit 6 | Ely1 | Grp6 | CTRL U1 | Cell Volt1 | CHAN BIT6 | BA01 | Electrical | 24 VDC | 24 VDC | Field bus | Undefined |  |  | DO | 0 | EIC | [5 empty] | ASHH |  | AH |  | AL |  | ASLL |  |  |  | =G01NHB06KF001+U012UNA01UH162-KF01 | 6ES7 132-6BF00-0BA0, DQ 8X24VDC/0,5A ST |  |  | 06 | =G01NHB06KF001&EFS.052 | =G01NHB06&MFB.001 |  |  | U012UNA01UH162
=G01NHE01BQ001 | G01NHE01BQ001-QM12 | =G01NHE01BQ001-QM12;XB02 | ELY1 O2 TRT QUAL SV12 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM12 | Solenoid valve | XB02 | Check back off/closed | Ely1 | O2 TRT | QUAL | SV12 | CB OFF/CLD | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF02 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG02:16 | 16d | 13 | =G01NHE01BQ001-QM12&EFS.002 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM12 | =G01NHE01BQ001-QM12;YB11 | ELY1 O2 TRT QUAL SV12 CMD ON/OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM12 | Solenoid valve | YB11 | Manual command ON/OPEN | Ely1 | O2 TRT | QUAL | SV12 | CMD ON/OP | -QM12MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DO | 0 | YS | [14 empty] | Not defined | =G01NHY01KF001+U012UNA01UH100-KF010 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 01 | =G01NHE01BQ001-QM12&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM13 | =G01NHE01BQ001-QM13;XB01 | ELY1 O2 TRT QUAL SV13 CB ON/OPN | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM13 | Solenoid valve | XB01 | Check back on/open | Ely1 | O2 TRT | QUAL | SV13 | CB ON/OPN | -QM13BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF02 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:37 | 37B | 02 | =G01NHE01BQ001-QM13&EFS.002 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM13 | =G01NHE01BQ001-QM13;XB02 | ELY1 O2 TRT QUAL SV13 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM13 | Solenoid valve | XB02 | Check back off/closed | Ely1 | O2 TRT | QUAL | SV13 | CB OFF/CLD | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF02 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG02:17 | 17d | 14 | =G01NHE01BQ001-QM13&EFS.002 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM13 | =G01NHE01BQ001-QM13;YB11 | ELY1 O2 TRT QUAL SV13 CMD ON/OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM13 | Solenoid valve | YB11 | Manual command ON/OPEN | Ely1 | O2 TRT | QUAL | SV13 | CMD ON/OP | -QM13MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DO | 0 | YS | [14 empty] | Not defined | =G01NHY01KF001+U012UNA01UH100-KF010 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 02 | =G01NHE01BQ001-QM13&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM14 | =G01NHE01BQ001-QM14;XB01 | ELY1 O2 TRT QUAL SV14 CB ON/OPN | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM14 | Solenoid valve | XB01 | Check back on/open | Ely1 | O2 TRT | QUAL | SV14 | CB ON/OPN | -QM14BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF02 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:42 | 42B | 03 | =G01NHE01BQ001-QM14&EFS.002 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM14 | =G01NHE01BQ001-QM14;XB02 | ELY1 O2 TRT QUAL SV14 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM14 | Solenoid valve | XB02 | Check back off/closed | Ely1 | O2 TRT | QUAL | SV14 | CB OFF/CLD | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF02 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG02:18 | 18d | 15 | =G01NHE01BQ001-QM14&EFS.002 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM14 | =G01NHE01BQ001-QM14;YB11 | ELY1 O2 TRT QUAL SV14 CMD ON/OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM14 | Solenoid valve | YB11 | Manual command ON/OPEN | Ely1 | O2 TRT | QUAL | SV14 | CMD ON/OP | -QM14MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DO | 0 | YS | [14 empty] | Not defined | =G01NHY01KF001+U012UNA01UH100-KF010 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 03 | =G01NHE01BQ001-QM14&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM15 | =G01NHE01BQ001-QM15;XB01 | ELY1 O2 TRT QUAL SV15 CB ON/OPN | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM15 | Solenoid valve | XB01 | Check back on/open | Ely1 | O2 TRT | QUAL | SV15 | CB ON/OPN | -QM15BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF02 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:47 | 47B | 04 | =G01NHE01BQ001-QM15&EFS.002 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM15 | =G01NHE01BQ001-QM15;XB02 | ELY1 O2 TRT QUAL SV15 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM15 | Solenoid valve | XB02 | Check back off/closed | Ely1 | O2 TRT | QUAL | SV15 | CB OFF/CLD | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF02 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG02:19 | 19d | 16 | =G01NHE01BQ001-QM15&EFS.002 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM15 | =G01NHE01BQ001-QM15;YB11 | ELY1 O2 TRT QUAL SV15 CMD ON/OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM15 | Solenoid valve | YB11 | Manual command ON/OPEN | Ely1 | O2 TRT | QUAL | SV15 | CMD ON/OP | -QM15MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DO | 0 | YS | [14 empty] | Not defined | =G01NHY01KF001+U012UNA01UH100-KF010 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 04 | =G01NHE01BQ001-QM15&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM16 | =G01NHE01BQ001-QM16;XB01 | ELY1 O2 TRT QUAL SV16 CB ON/OPN | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM16 | Solenoid valve | XB01 | Check back on/open | Ely1 | O2 TRT | QUAL | SV16 | CB ON/OPN | -QM16BG01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF02 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG01:52 | 52B | 05 | =G01NHE01BQ001-QM16&EFS.002 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHC01GT001 | G01NHC01GT001-QM01 | =G01NHC01GT001-QM01;YB12 | ELY1 H2 TRT LEAD OFF SV1 CMD OFF/CL | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 H2 TREATMENT H2 TREATMENT SYSTEM GAS LEAD OFF SYSTEMS GAS LEAD OFF SYSTEM 1 2-WAY SHUT-OFF VALVE H2 MANUAL COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHC | H2 Treatment | 01 | H2 Treatment System | GT | Gas Lead off Systems | 001 | Gas Lead off System 1 | -QM01 | 2-way shut-off valve H2 | YB12 | Manual command OFF/CLOSE | Ely1 | H2 TRT | Lead Off | SV1 | CMD OFF/CL | -QM01MB01 | Electrical | 24 VDC | 24 VDC | Wire | Continuous signal |  |  | DO | 0 | YS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF09 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB12 | EA01 | 13 | =G01NHC01GT001-QM01&EFS.001 | =G01NHC01&MFB.002 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM16 | =G01NHE01BQ001-QM16;XB02 | ELY1 O2 TRT QUAL SV16 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM16 | Solenoid valve | XB02 | Check back off/closed | Ely1 | O2 TRT | QUAL | SV16 | CB OFF/CLD | -XG02 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DI | 1 | GZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF02 | 6ES7 326-1BK02-0AB0, SM 326, F-DI 24 X DC24V, FAILSAFE | XG02:20 | 20d | 17 | =G01NHE01BQ001-QM16&EFS.002 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM16 | =G01NHE01BQ001-QM16;YB11 | ELY1 O2 TRT QUAL SV16 CMD ON/OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM16 | Solenoid valve | YB11 | Manual command ON/OPEN | Ely1 | O2 TRT | QUAL | SV16 | CMD ON/OP | -QM16MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DO | 0 | YS | [14 empty] | Not defined | =G01NHY01KF001+U012UNA01UH100-KF010 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 05 | =G01NHE01BQ001-QM16&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM23 | =G01NHE01BQ001-QM23;XB11 | ELY1 O2 TRT QUAL SV23 CB MAN ON/OPN | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM 3-WAY VALVE - CAL-GAS MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM23 | 3-way Valve - Cal-Gas | XB11 | Manual command ON/OPEN | Ely1 | O2 TRT | QUAL | SV23 | CB MAN ON/OPN | -QM23BG01 | Electrical | 24 VAC | 24 VAC | Wire | Undefined |  |  | DI | 0 | GS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB11 | EA01 | 11 | =G01NHE01BQ001-QM23&EFS.002 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM24 | =G01NHE01BQ001-QM24;XB01 | ELY1 O2 TRT QUAL SV24 CB ON/OPN | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM24 | Solenoid valve | XB01 | Check back on/open | Ely1 | O2 TRT | QUAL | SV24 | CB ON/OPN | -QM24BG01 | Electrical | 24 VAC | 24 VAC | Wire | Normally opened |  |  | DI | 0 | GZ | [13 empty] | Yes |  | =G01NHY01KF001+U012UNA01UH100-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB01 | XB01 | 12 | =G01NHE01BQ001-QM24&EFS.002 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM24 | =G01NHE01BQ001-QM24;XB02 | ELY1 O2 TRT QUAL SV24 CB OFF/CLD | 32 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE CHECK BACK OFF/CLOSED | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM24 | Solenoid valve | XB02 | Check back off/closed | Ely1 | O2 TRT | QUAL | SV24 | CB OFF/CLD | -XG01 | Electrical | 24 VAC | 24 VAC | Wire | Normally opened |  |  | DI | 0 | GZ | [13 empty] | Yes |  | =G01NHY01KF001+U012UNA01UH100-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB02 | XB02 | 13 | =G01NHE01BQ001-QM24&EFS.002 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM24 | =G01NHE01BQ001-QM24;YB11 | ELY1 O2 TRT QUAL SV24 CMD ON/OP | 31 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM SOLENOID VALVE MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM24 | Solenoid valve | YB11 | Manual command ON/OPEN | Ely1 | O2 TRT | QUAL | SV24 | CMD ON/OP | -QM24MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DO | 0 | YS | [14 empty] | Not defined | =G01NHY01KF001+U012UNA01UH100-KF010 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 06 | =G01NHE01BQ001-QM24&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QM27 | =G01NHE01BQ001-QM27;XB11 | ELY1 O2 TRT QUAL SV27 CB MAN ON/OPN | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM 3-WAY VALVE - CAL-GAS MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QM27 | 3-way Valve - Cal-Gas | XB11 | Manual command ON/OPEN | Ely1 | O2 TRT | QUAL | SV27 | CB MAN ON/OPN | -QM27BG01 | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DI | 0 | GS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB11 | EA01 | 14 | =G01NHE01BQ001-QM27&EFS.002 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-QN22 | =G01NHE01BQ001-QN22;XG01 | ELY1 O2 TRT QUAL PRES22 CB ON/OPN/MAX1 | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM PRESSURE GAUGE WITH PRESSURE SWITCH CHECK BACK ON/OPEN // LIMIT VALUE >MAX 1 | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -QN22 | Pressure gauge with pressure switch | XG01 | Check back on/open // Limit value >max 1 | Ely1 | O2 TRT | QUAL | Pres22 | CB ON/OPN/MAX1 | -QN22 | Electrical | 24 VAC | 24 VAC | Wire | Undefined |  |  | DI | 0 | PS | [9 empty] | ASL | [5 empty] | =G01NHY01KF001+U012UNA01UH100-KF03 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XG01 | EA01 | 16 | =G01NHE01BQ001-QN22&EFS.001 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHE01BQ001 | G01NHE01BQ001-SF01 | =G01NHE01BQ001-SF01;XB11 | ELY1 O2 TRT QUAL SW OFF CB MAN ON/OPN | 37 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 O2 TREATMENT O2 TREATMENT SYSTEM QUALITY MEASURING SYSTEMS H2 IN O2 MEASURING SYSTEM KEY-SWITCH - MAINTENANCE ON/OFF MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHE | O2 Treatment | 01 | O2 Treatment System | BQ | Quality Measuring Systems | 001 | H2 in O2 Measuring System | -SF01 | Key-switch - Maintenance on/off | XB11 | Manual command ON/OPEN | Ely1 | O2 TRT | QUAL | Sw OFF | CB MAN ON/OPN | -XG01 | Electrical | 24 VAC | 24 VAC | Wire | Undefined |  |  | DI | 0 | HC | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF04 | 6DL1 131-6BH00-0EH1, ET 200SP HA, DI 16X24VDC | B10:XB11 | EA01 | 15 | =G01NHE01BQ001-SF01&EFS.002 | =G01NHE01&MFB.003 |  |  | U012UNA01UH100
=G01NHG01QM001 | G01NHG01QM001-QM01 | =G01NHG01QM001-QM01;YB11 | ELY1 PROC WTR SUP DIST SV1 CMD ON/OP | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 WATER SUPPLY SYSTEMS PROCESS WATER SUPPLY SYSTEM PROCESS WATER DISTRIBUTION SYSTEMS PROCESS WATER DISTRIBUTION SYSTEM 2-WAY SHUT-OFF VALVE - DEMIN WATER SUPPLY MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHG | Water Supply Systems | 01 | Process Water Supply System | QM | Process Water Distribution Systems | 001 | Process Water Distribution System | -QM01 | 2-way shut-off valve - Demin water supply | YB11 | Manual command ON/OPEN | Ely1 | Proc Wtr Sup | DIST | SV1 | CMD ON/OP | -QM01MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally closed |  |  | DO | 0 | YS | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF010 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10:YB11 | EA01 | 07 | =G01NHG01QM001-QM01&EFS.001 | =G01NHC01&MFB.001 |  |  | U012UNA01UH100
=G01NHH01HP001 | G01NHH01HP001-GP01 | =G01NHH01HP001-GP01;YV01 | ELY1 PROC WTR REF SYS 1 PMP1 INTLK1 | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 PROCESS WATER REFINEMENT PROCESS WATER REFINEMENT LOOP PROCESS WATER REFINEMENT UNIT PROCESS WATER REFINEMENT UNIT 1 WATER REFINEMENT CIRCULATION PUMP SIGNAL INTERLOCK | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHH | Process Water Refinement | 01 | Process Water Refinement Loop | HP | Process Water Refinement Unit | 001 | Process Water Refinement Unit 1 | -GP01 | Water Refinement Circulation Pump | YV01 | Signal interlock | Ely1 | Proc Wtr Ref | SYS 1 | PMP1 | INTLK1 | DR | Electrical | 24 VDC | 24 VDC | Wire | Undefined |  |  | DO | 0 | NC | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF010 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | B10_1:YV01 | EA01 | 09 | =G01NHH01HP001-GP01&EFS.001 | =G01NHH01&MFB.001 |  |  | U012UNA01UH100
=G01NHH01HP001 | G01NHH01HP001-GP01 | =G01NHH01HP001-GP01;YB11 | ELY1 PROC WTR REF SYS 1 PMP1 CMD ON/OP | 38 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 PROCESS WATER REFINEMENT PROCESS WATER REFINEMENT LOOP PROCESS WATER REFINEMENT UNIT PROCESS WATER REFINEMENT UNIT 1 WATER REFINEMENT CIRCULATION PUMP MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHH | Process Water Refinement | 01 | Process Water Refinement Loop | HP | Process Water Refinement Unit | 001 | Process Water Refinement Unit 1 | -GP01 | Water Refinement Circulation Pump | YB11 | Manual command ON/OPEN | Ely1 | Proc Wtr Ref | SYS 1 | PMP1 | CMD ON/OP | DR | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 0 | NC | [15 empty] | =G01NHY01KF001+U012UNA01UH100-KF010 | 6DL1 132-6BH00-0EH1, ET 200SP HA, DQ 16X24VDC/0,5A | XD02:1 | 1B | 08 | =G01NHH01HP001-GP01&EFS.001 | =G01NHH01&MFB.001 |  |  | U012UNA01UH100
=G01NHX01QN001 | G01NHX01QN001-QM11 | =G01NHX01QN001-QM11;YB12 | ELY1 N2 DIST CTRL H2 SV11 CMD OFF/CL | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION H2 BALL VALVE - NITROGEN H2 BYPASS MANUAL COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 001 | Nitrogen Regulation H2 | -QM11 | Ball valve - Nitrogen H2 bypass | YB12 | Manual command OFF/CLOSE | Ely1 | N2 Dist | CTRL H2 | SV11 | CMD OFF/CL | -QM11MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 1 | YZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF03 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | XG01:8 | 8B | 01 | =G01NHX01QN001-QM11&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=G01NHX01QN001 | G01NHX01QN001-QM21 | =G01NHX01QN001-QM21;YB12 | ELY1 N2 DIST CTRL H2 SV21 CMD OFF/CL | 36 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION H2 BALL VALVE - NITROGEN H2 OUTLET MANUAL COMMAND OFF/CLOSE | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 001 | Nitrogen Regulation H2 | -QM21 | Ball valve - Nitrogen H2 outlet | YB12 | Manual command OFF/CLOSE | Ely1 | N2 Dist | CTRL H2 | SV21 | CMD OFF/CL | -QM21MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 1 | YZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF03 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | XG01:14 | 14B | 02 | =G01NHX01QN001-QM21&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=G01NHX01QN002 | G01NHX01QN002-QM11 | =G01NHX01QN002-QM11;YB11 | ELY1 N2 DIST CTRL O2 SV11 CMD ON/OP | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION O2 BALL VALVE - NITROGEN O2 BYPASS MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 002 | Nitrogen Regulation O2 | -QM11 | Ball valve - Nitrogen O2 bypass | YB11 | Manual command ON/OPEN | Ely1 | N2 Dist | CTRL O2 | SV11 | CMD ON/OP | -QM11MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 1 | YS | [13 empty] | No | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF03 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | XG01:30 | 30B | 03 | =G01NHX01QN002-QM11&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=G01NHX01QN002 | G01NHX01QN002-QM21 | =G01NHX01QN002-QM21;YB11 | ELY1 N2 DIST CTRL O2 SV21 CMD ON/OP | 35 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 AUXILIARY SYSTEMS NITROGEN DISTRIBUTION NITROGEN REGULATION SYSTEMS NITROGEN REGULATION O2 BALL VALVE - NITROGEN O2 OUTLET MANUAL COMMAND ON/OPEN | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHX | Auxiliary Systems | 01 | Nitrogen Distribution | QN | Nitrogen Regulation Systems | 002 | Nitrogen Regulation O2 | -QM21 | Ball valve - Nitrogen O2 outlet | YB11 | Manual command ON/OPEN | Ely1 | N2 Dist | CTRL O2 | SV21 | CMD ON/OP | -QM21MB01 | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 1 | YZ | [13 empty] | Yes | SIL 2 | =G01NHY01KF001+U012UNA01UH100-KF03 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | XG01:36 | 36B | 04 | =G01NHX01QN002-QM21&EFS.001 | =G01NHX01&MFB.001 |  |  | U012UNA01UH100
=T01BBA01QA001 | T01BBA01QA001-QA01 | =T01BBA01QA001-QA01;YW01 | EL POW SUP MV MV DIST1 SW1 AL/PROT1 | 35 | ELECTRICAL POWER SUPPLY SYSTEM SYSTEM 1 MV SUPPLY SYSTEM - 20KV SYSTEM 1 MV DISTRIBUTION MV DISTRIBUTION UNIT - ARRAY 1 POWER CIRCUIT-BREAKER, 3-POLE COMPONENT PROTECTION | =T | Electrical Power Supply System | 01 | System 1 | BBA | MV Supply System - 20kV | 01 | System 1 | QA | MV Distribution | 001 | MV Distribution Unit - Array 1 | -QA01 | Power circuit-breaker, 3-pole | YW01 | Component protection | El Pow Sup | MV | MV DIST1 | Sw1 | AL/PROT1 | -XG03 | Electrical |  |  | Wire | Undefined |  |  | DO | 1 | YSZ | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | B10:YW01 | YW01 | 03 | =T01BBA01QA001-QA01&EFS.004 |  |  |  | U012UBB01UC001
=T01BBA01QA001 | T01BBA01QA001-QA01 | =T01BBA01QA001-QA01;YB11 | EL POW SUP MV MV DIST1 SW1 CMD ON/OP | 36 | ELECTRICAL POWER SUPPLY SYSTEM SYSTEM 1 MV SUPPLY SYSTEM - 20KV SYSTEM 1 MV DISTRIBUTION MV DISTRIBUTION UNIT - ARRAY 1 POWER CIRCUIT-BREAKER, 3-POLE MANUAL COMMAND ON/OPEN | =T | Electrical Power Supply System | 01 | System 1 | BBA | MV Supply System - 20kV | 01 | System 1 | QA | MV Distribution | 001 | MV Distribution Unit - Array 1 | -QA01 | Power circuit-breaker, 3-pole | YB11 | Manual command ON/OPEN | El Pow Sup | MV | MV DIST1 | Sw1 | CMD ON/OP | -XG03 | Electrical |  |  | Wire | Undefined |  |  | DO | 1 | YSZ | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | B10:YB11 | YB11 | 01 | =T01BBA01QA001-QA01&EFS.001 |  |  |  | U012UBB01UC001
=T01BBA01QA001 | T01BBA01QA001-QA01 | =T01BBA01QA001-QA01;YB12 | EL POW SUP MV MV DIST1 SW1 CMD OFF/CL | 37 | ELECTRICAL POWER SUPPLY SYSTEM SYSTEM 1 MV SUPPLY SYSTEM - 20KV SYSTEM 1 MV DISTRIBUTION MV DISTRIBUTION UNIT - ARRAY 1 POWER CIRCUIT-BREAKER, 3-POLE MANUAL COMMAND OFF/CLOSE | =T | Electrical Power Supply System | 01 | System 1 | BBA | MV Supply System - 20kV | 01 | System 1 | QA | MV Distribution | 001 | MV Distribution Unit - Array 1 | -QA01 | Power circuit-breaker, 3-pole | YB12 | Manual command OFF/CLOSE | El Pow Sup | MV | MV DIST1 | Sw1 | CMD OFF/CL | -XG03 | Electrical |  |  | Wire | Undefined |  |  | DO | 1 | YSZ | [15 empty] | =G01NHA01KF001+U012UBB01UC001-KF03 | 6ES7 326-2BF10-0AB0, SM 326, 10DO, DC 24V, 2A PP, failsafe | B10:YB12 | YB12 | 02 | =T01BBA01QA001-QA01&EFS.001 |  |  |  | U012UBB01UC001
=V01NHC30WP001 | V01NHC30WP001-QM02 | =V01NHC30WP001-QM02;YB12 | GAS TRT H2 COMPR PIPING SV2 CMD OFF/CL | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 30BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM INLET LINE 2-WAY SHUT-OFF VALVE (GENERAL) MANUAL COMMAND OFF/CLOSE | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 30 | H2 Compressor System 30bar | WP | Compressor Pipe Systems | 001 | Compressor Pipe System Inlet Line | -QM02 | 2-way shut-off valve (general) | YB12 | Manual command OFF/CLOSE | Gas TRT | H2 Compr | Piping | SV2 | CMD OFF/CL |  | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 0 | YS | [21 empty] | =V01NHC30&MFB.001
=V01NHC30WP001 | V01NHC30WP001-QM03 | =V01NHC30WP001-QM03;YB12 | GAS TRT H2 COMPR PIPING SV3 CMD OFF/CL | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 30BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM INLET LINE BALL VALVE (GENERAL) MANUAL COMMAND OFF/CLOSE | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 30 | H2 Compressor System 30bar | WP | Compressor Pipe Systems | 001 | Compressor Pipe System Inlet Line | -QM03 | Ball valve (general) | YB12 | Manual command OFF/CLOSE | Gas TRT | H2 Compr | Piping | SV3 | CMD OFF/CL |  | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 0 | YS | [21 empty] | =V01NHC30&MFB.001
=V01NHC30WP001 | V01NHC30WP001-QM06 | =V01NHC30WP001-QM06;YB12 | GAS TRT H2 COMPR PIPING SV6 CMD OFF/CL | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 30BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM INLET LINE BUTTERFLY VALVE (GEN.) MANUAL COMMAND OFF/CLOSE | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 30 | H2 Compressor System 30bar | WP | Compressor Pipe Systems | 001 | Compressor Pipe System Inlet Line | -QM06 | Butterfly valve (gen.) | YB12 | Manual command OFF/CLOSE | Gas TRT | H2 Compr | Piping | SV6 | CMD OFF/CL |  | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 0 | YS | [21 empty] | =V01NHC30&MFB.001
=V01NHC30WP002 | V01NHC30WP002-QM01 | =V01NHC30WP002-QM01;YB12 | GAS TRT H2 COMPR PIPING SV1 CMD OFF/CL | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 30BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM OUTLET LINE BALL VALVE (GENERAL) MANUAL COMMAND OFF/CLOSE | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 30 | H2 Compressor System 30bar | WP | Compressor Pipe Systems | 002 | Compressor Pipe System Outlet Line | -QM01 | Ball valve (general) | YB12 | Manual command OFF/CLOSE | Gas TRT | H2 Compr | Piping | SV1 | CMD OFF/CL |  | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 0 | YS | [21 empty] | =V01NHC30&MFB.001
=V01NHC31WP001 | V01NHC31WP001-QM01 | =V01NHC31WP001-QM01;YB12 | GAS TRT H2 COMPR PIPING SV1 CMD OFF/CL | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 100BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM INLET LINE BUTTERFLY VALVE (GEN.) MANUAL COMMAND OFF/CLOSE | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 31 | H2 Compressor System 100bar | WP | Compressor Pipe Systems | 001 | Compressor Pipe System Inlet Line | -QM01 | Butterfly valve (gen.) | YB12 | Manual command OFF/CLOSE | Gas TRT | H2 Compr | Piping | SV1 | CMD OFF/CL |  | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 0 | YS | [21 empty] | =V01NHC31&MFB.001
=V01NHC31WP001 | V01NHC31WP001-QM02 | =V01NHC31WP001-QM02;YB12 | GAS TRT H2 COMPR PIPING SV2 CMD OFF/CL | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 100BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM INLET LINE 2-WAY SHUT-OFF VALVE (GENERAL) MANUAL COMMAND OFF/CLOSE | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 31 | H2 Compressor System 100bar | WP | Compressor Pipe Systems | 001 | Compressor Pipe System Inlet Line | -QM02 | 2-way shut-off valve (general) | YB12 | Manual command OFF/CLOSE | Gas TRT | H2 Compr | Piping | SV2 | CMD OFF/CL |  | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 0 | YS | [21 empty] | =V01NHC31&MFB.001
=V01NHC31WP001 | V01NHC31WP001-QM03 | =V01NHC31WP001-QM03;YB12 | GAS TRT H2 COMPR PIPING SV3 CMD OFF/CL | 38 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT H2 COMPRESSOR SYSTEM 100BAR COMPRESSOR PIPE SYSTEMS COMPRESSOR PIPE SYSTEM INLET LINE BALL VALVE (GENERAL) MANUAL COMMAND OFF/CLOSE | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 31 | H2 Compressor System 100bar | WP | Compressor Pipe Systems | 001 | Compressor Pipe System Inlet Line | -QM03 | Ball valve (general) | YB12 | Manual command OFF/CLOSE | Gas TRT | H2 Compr | Piping | SV3 | CMD OFF/CL |  | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 0 | YS | [21 empty] | =V01NHC31&MFB.001
=V01NHC60BZ001 | V01NHC60BZ001-QM01 | =V01NHC60BZ001-QM01;YB12 | GAS TRT H2 HANDOVR MEAS1 SV1 CMD OFF/CL | 39 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIC SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 BALL VALVE (GENERAL) MANUAL COMMAND OFF/CLOSE | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 60 | Product Gas Analytic System | BZ | Measurement Systems | 001 | Measurement System 1 | -QM01 | Ball valve (general) | YB12 | Manual command OFF/CLOSE | Gas TRT | H2 Handovr | Meas1 | SV1 | CMD OFF/CL |  | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 0 | YS | [21 empty] | =V01NHC60&MFB.001
=V01NHC60BZ001 | V01NHC60BZ001-QM02 | =V01NHC60BZ001-QM02;YB12 | GAS TRT H2 HANDOVR MEAS1 SV2 CMD OFF/CL | 39 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIC SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 BALL VALVE (GENERAL) MANUAL COMMAND OFF/CLOSE | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 60 | Product Gas Analytic System | BZ | Measurement Systems | 001 | Measurement System 1 | -QM02 | Ball valve (general) | YB12 | Manual command OFF/CLOSE | Gas TRT | H2 Handovr | Meas1 | SV2 | CMD OFF/CL |  | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 0 | YS | [21 empty] | =V01NHC60&MFB.001
=V01NHC60BZ001 | V01NHC60BZ001-QM03 | =V01NHC60BZ001-QM03;YB12 | GAS TRT H2 HANDOVR MEAS1 SV3 CMD OFF/CL | 39 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIC SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 BALL VALVE (GENERAL) MANUAL COMMAND OFF/CLOSE | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 60 | Product Gas Analytic System | BZ | Measurement Systems | 001 | Measurement System 1 | -QM03 | Ball valve (general) | YB12 | Manual command OFF/CLOSE | Gas TRT | H2 Handovr | Meas1 | SV3 | CMD OFF/CL |  | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 0 | YS | [21 empty] | =V01NHC60&MFB.001
=V01NHC61BZ001 | V01NHC61BZ001-QM01 | =V01NHC61BZ001-QM01;YB12 | GAS TRT H2 HANDOVR MEAS1 SV1 CMD OFF/CL | 39 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIK SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 BALL VALVE (GENERAL) MANUAL COMMAND OFF/CLOSE | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 61 | Product Gas Analytik System | BZ | Measurement Systems | 001 | Measurement System 1 | -QM01 | Ball valve (general) | YB12 | Manual command OFF/CLOSE | Gas TRT | H2 Handovr | Meas1 | SV1 | CMD OFF/CL |  | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 0 | YS | [21 empty] | =V01NHC61&MFB.001
=V01NHC61BZ001 | V01NHC61BZ001-QM02 | =V01NHC61BZ001-QM02;YB12 | GAS TRT H2 HANDOVR MEAS1 SV2 CMD OFF/CL | 39 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIK SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 BALL VALVE (GENERAL) MANUAL COMMAND OFF/CLOSE | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 61 | Product Gas Analytik System | BZ | Measurement Systems | 001 | Measurement System 1 | -QM02 | Ball valve (general) | YB12 | Manual command OFF/CLOSE | Gas TRT | H2 Handovr | Meas1 | SV2 | CMD OFF/CL |  | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 0 | YS | [21 empty] | =V01NHC61&MFB.001
=V01NHC61BZ001 | V01NHC61BZ001-QM03 | =V01NHC61BZ001-QM03;YB12 | GAS TRT H2 HANDOVR MEAS1 SV3 CMD OFF/CL | 39 | GAS TREATMENT SYSTEM GAS TREATMENT SYSTEM 1 H2 TREATMENT PRODUCT GAS ANALYTIK SYSTEM MEASUREMENT SYSTEMS MEASUREMENT SYSTEM 1 BALL VALVE (GENERAL) MANUAL COMMAND OFF/CLOSE | =V | Gas Treatment System | 01 | Gas Treatment System 1 | NHC | H2 Treatment | 61 | Product Gas Analytik System | BZ | Measurement Systems | 001 | Measurement System 1 | -QM03 | Ball valve (general) | YB12 | Manual command OFF/CLOSE | Gas TRT | H2 Handovr | Meas1 | SV3 | CMD OFF/CL |  | Electrical | 24 VDC | 24 VDC | Wire | Normally opened |  |  | DO | 0 | YS | [21 empty] | =V01NHC61&MFB.001
=G01NHA01EQ001 | G01NHA01EQ001-KZ01 |  | ELY1 RECT1 COOL AUTOM FKT ANALOG1 | 33 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 COOLING SYSTEMS RECTIFIER COOLING SYSTEM DIFFERENTIAL PRESSURE PUMP ANALOG PROCESS SIGNAL | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | EQ | Cooling Systems | 001 | Rectifier Cooling System | -KZ01 | Differential Pressure Pump | XQ01 | Analog process signal | Ely1 | Rect1 | Cool | AUTOM FKT | ANALOG1 |  | Software |  |  | None | Undefined |  |  |  |  | UD | [5 empty] | ASHH |  | AH | [13 empty] | =G01NHA01&MFB.001
=G01NHA01TB001 | G01NHA01TB001-BC01 |  | ELY1 RECT1 RECT1 CURR1 ANALOG1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 1 CURRENT TRANSFORMER - U AC CURRENT MEASUREMENT - PHASE U | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 001 | Rectifier 1 | -BC01 | Current transformer - U | XQ01 | AC Current Measurement - Phase U | Ely1 | Rect1 | Rect1 | Curr1 | ANALOG1 | DR | Electrical |  |  | None | Undefined |  |  |  |  | I
=G01NHA01TB001 | G01NHA01TB001-BC02 |  | ELY1 RECT1 RECT1 CURR2 ANALOG1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 1 CURRENT TRANSFORMER - V AC CURRENT MEASUREMENT - PHASE V | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 001 | Rectifier 1 | -BC02 | Current transformer - V | XQ01 | AC Current Measurement - Phase V | Ely1 | Rect1 | Rect1 | Curr2 | ANALOG1 | DR | Electrical |  |  | None | Undefined |  |  |  |  | I
=G01NHA01TB001 | G01NHA01TB001-BC03 |  | ELY1 RECT1 RECT1 CURR3 ANALOG1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 1 CURRENT TRANSFORMER - W AC CURRENT MEASUREMENT - PHASE W | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 001 | Rectifier 1 | -BC03 | Current transformer - W | XQ01 | AC Current Measurement - Phase W | Ely1 | Rect1 | Rect1 | Curr3 | ANALOG1 | DR | Electrical |  |  | None | Undefined |  |  |  |  | I
=G01NHA01TB002 | G01NHA01TB002-BC01 |  | ELY1 RECT1 RECT2 CURR1 ANALOG1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 2 CURRENT TRANSFORMER - U AC CURRENT MEASUREMENT - PHASE U | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 002 | Rectifier 2 | -BC01 | Current transformer - U | XQ01 | AC Current Measurement - Phase U | Ely1 | Rect1 | Rect2 | Curr1 | ANALOG1 | DR | Electrical |  |  | None | Undefined |  |  |  |  | I
=G01NHA01TB002 | G01NHA01TB002-BC02 |  | ELY1 RECT1 RECT2 CURR2 ANALOG1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 2 CURRENT TRANSFORMER - V AC CURRENT MEASUREMENT - PHASE V | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 002 | Rectifier 2 | -BC02 | Current transformer - V | XQ01 | AC Current Measurement - Phase V | Ely1 | Rect1 | Rect2 | Curr2 | ANALOG1 | DR | Electrical |  |  | None | Undefined |  |  |  |  | I
=G01NHA01TB002 | G01NHA01TB002-BC03 |  | ELY1 RECT1 RECT2 CURR3 ANALOG1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 2 CURRENT TRANSFORMER - W AC CURRENT MEASUREMENT - PHASE W | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 002 | Rectifier 2 | -BC03 | Current transformer - W | XQ01 | AC Current Measurement - Phase W | Ely1 | Rect1 | Rect2 | Curr3 | ANALOG1 | DR | Electrical |  |  | None | Undefined |  |  |  |  | I
=G01NHA01TB003 | G01NHA01TB003-BC01 |  | ELY1 RECT1 RECT3 CURR1 ANALOG1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 3 CURRENT TRANSFORMER - U AC CURRENT MEASUREMENT - PHASE U | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 003 | Rectifier 3 | -BC01 | Current transformer - U | XQ01 | AC Current Measurement - Phase U | Ely1 | Rect1 | Rect3 | Curr1 | ANALOG1 | DR | Electrical |  |  | None | Undefined |  |  |  |  | I
=G01NHA01TB003 | G01NHA01TB003-BC02 |  | ELY1 RECT1 RECT3 CURR2 ANALOG1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 3 CURRENT TRANSFORMER - V AC CURRENT MEASUREMENT - PHASE V | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 003 | Rectifier 3 | -BC02 | Current transformer - V | XQ01 | AC Current Measurement - Phase V | Ely1 | Rect1 | Rect3 | Curr2 | ANALOG1 | DR | Electrical |  |  | None | Undefined |  |  |  |  | I
=G01NHA01TB003 | G01NHA01TB003-BC03 |  | ELY1 RECT1 RECT3 CURR3 ANALOG1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 3 CURRENT TRANSFORMER - W AC CURRENT MEASUREMENT - PHASE W | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 003 | Rectifier 3 | -BC03 | Current transformer - W | XQ01 | AC Current Measurement - Phase W | Ely1 | Rect1 | Rect3 | Curr3 | ANALOG1 | DR | Electrical |  |  | None | Undefined |  |  |  |  | I
=G01NHA01TB004 | G01NHA01TB004-BC01 |  | ELY1 RECT1 RECT4 CURR1 ANALOG1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 4 CURRENT TRANSFORMER - U AC CURRENT MEASUREMENT - PHASE U | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 004 | Rectifier 4 | -BC01 | Current transformer - U | XQ01 | AC Current Measurement - Phase U | Ely1 | Rect1 | Rect4 | Curr1 | ANALOG1 | DR | Electrical |  |  | None | Undefined |  |  |  |  | I
=G01NHA01TB004 | G01NHA01TB004-BC02 |  | ELY1 RECT1 RECT4 CURR2 ANALOG1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 4 CURRENT TRANSFORMER - V AC CURRENT MEASUREMENT - PHASE V | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 004 | Rectifier 4 | -BC02 | Current transformer - V | XQ01 | AC Current Measurement - Phase V | Ely1 | Rect1 | Rect4 | Curr2 | ANALOG1 | DR | Electrical |  |  | None | Undefined |  |  |  |  | I
=G01NHA01TB004 | G01NHA01TB004-BC03 |  | ELY1 RECT1 RECT4 CURR3 ANALOG1 | 30 | ELECTROLYSIS SYSTEM ELECTROLYSIS ARRAY 1 RECTIFIER SYSTEMS RECTIFIER SYSTEM 1 RECTIFIERS RECTIFIER 4 CURRENT TRANSFORMER - W AC CURRENT MEASUREMENT - PHASE W | =G | Electrolysis System | 01 | Electrolysis Array 1 | NHA | Rectifier Systems | 01 | Rectifier System 1 | TB | Rectifiers | 004 | Rectifier 4 | -BC03 | Current transformer - W | XQ01 | AC Current Measurement - Phase W | Ely1 | Rect1 | Rect4 | Curr3 | ANALOG1 | DR | Electrical |  |  | None | Undefined |  |  |  |  | I
=T01BBA01QA001 | T01BBA01QA001-QA01 |  | EL POW SUP MV MV DIST1 SW1 GRP FLT | 34 | ELECTRICAL POWER SUPPLY SYSTEM SYSTEM 1 MV SUPPLY SYSTEM - 20KV SYSTEM 1 MV DISTRIBUTION MV DISTRIBUTION UNIT - ARRAY 1 POWER CIRCUIT-BREAKER, 3-POLE CIRCUIT BREAKER TRIPPING | =T | Electrical Power Supply System | 01 | System 1 | BBA | MV Supply System - 20kV | 01 | System 1 | QA | MV Distribution | 001 | MV Distribution Unit - Array 1 | -QA01 | Power circuit-breaker, 3-pole | XU01 | Circuit breaker tripping | El Pow Sup | MV | MV DIST1 | Sw1 | GRP FLT |  | Electrical |  |  |  | Undefined |  |  |  |  | GH